Access Control System

Specifier Notes typically precede specification text; delete notes in final copy of specification. Trade/brand names with appropriate symbols typically are used in Specifier Notes; symbols are not used in specification text. Metric conversion, where used, is soft metric conversion.

.

SECTION 28 13 00
ACCESS CONTROL 

PART 1	- GENERAL

1.1	SUMMARY
A.	Section Includes: Server hardware and software, client software, security access devices, access control, relay control, elevator control, credential creation and credential holder database and management, Digital Video Integration, Basic Burglary Alarm Integration
Specifier Note: Revise paragraph below to suit project requirements. Add section numbers and titles per CSI MasterFormat and specifier’s practice.
B.	Related Sections:
1.	Section [08 11 00 - Metal Doors and Frames] [_____].
2.	Section [08 14 00 - Wood Doors] [_____].
3.	Section [08 41 13 – Aluminum Framed Entrances and Store fronts] [_____]
4.	Section [08 71 00 - Door Hardware] [_____].
5.	Section [14 20 00 - Elevators] [_____].
6.	Section [21 09 00 – Instrumentation and Control for Fire-Suppression Systems] [_____]
7.	Section [25 15 00 - Integrated Automation Software] [_____].
8.	Section [26 05 00 - Common Work Results for Electrical] [_____].
9.	Section [26 05 19 - Low-Voltage Electrical Power Conductors and Cables] [_____].
10.	Section [27 10 00 - Structured Cabling] [_____].
Specifier Note: Article below may be omitted when specifying manufacturer’s proprietary products and recommended installation. Retain Reference Article when specifying products and installation by an industry reference standard. If retained, list standard(s) referenced in this section. Indicate issuing authority name, acronym, standard designation and title. Establish policy for indicating edition date of standard referenced. Conditions of the Contract or Section 01 42 19 - Reference Standards may establish the edition date of standards. This article does not require compliance with standard, but is merely a listing of references used. Article below should list only those industry standards referenced in this section. Retain only those reference standards to be used within the text of this Section. Add and delete as required for specific project.
1.2	REFERENCES
A.	Institute of Electrical and Electronics Engineers (IEEE):
1.	IEEE 1100 Recommended Practice for Powering and Grounding Electronic Equipment.
B.	National Fire Protection Association (NFPA):
1.	NFPA 70 2005 National Electrical Code.
2.	NFPA 72 National Fire Alarm Code.
3.	NFPA 80 Fire Doors and Windows, 2007 Edition.
4.	NFPA 101 Life Safety Code, 2009 Edition.
C.	International Organization for Standardization (ISO):
1.	ISO 7816 Smart Card Standard.

Specifier Note: Article below should be restricted to statements describing design or performance requirements and functional (not dimensional) tolerances of a complete system. Limit descriptions to composite and operational properties required to link components of a system together and to interface with other systems.

1.3	SYSTEM DESCRIPTION
A.	Design Requirements: Shall provide products and systems that have been manufactured, fabricated and installed to the following criteria:
1.	Comply with IEEE 1100.
2.	Comply with NFPA 70.
3.	Comply with NFPA 72.
4.	Comply with NFPA 80.
5.	Comply with NFPA 101.
6.	Access Control Management System: Vicon Electronic Access Control System.
a.	System Capabilities:
1)	Stand-alone or networked.
2)	Control access to unlimited doors.
3)	Control elevator access up to 64 floors per Cab.
4)	Manage and control access for up to 100,000 credentials per controller.
5)	Unlimited remote sites.
6)	Configurable alert screen and email notifications
7)	Photo ID badging integration via SQL database
8)	Readers, inputs and outputs expandable and/or modifiable.
9)	Single software program controlled.
10)	50 Programmable Holidays per Holiday Group
11)	50 Holiday Groups configurable
12)	Multi-site Management via Partitions
13)	No client software needed, client accesses via HTML5 browser
14)	Local anti-passback
15)	Full integration and customization of all system components.
16)	Online reconfiguration through system programming without hardware changes.
b.	Access Control Functions:
1)	Validation of Credential based on Time of day, Day of week, Holiday scheduling, mode of Door, and ad-hock schedule.
2)	Simultaneous controlled access with various reader technologies; 
a)	Proximity
b)	Pin number
c)	Biometrics
d)	Mag stripe
e)	barcode
3)	Automatic or manual retrieval of cardholder photographs.
4)	First person in capability.
5)	Access validation based on positive verification of Credential, PIN, or Credential/PIN combination, or dual credential with one credential being a supervisor credential.
6)	Differentiates between valid credential presentation only, and valid credential presentation followed by entry (when using door position switch).

c.	Passwords:
1)	Assignable.
2)	Unlimited number of system Administrators.
3)	Permissions of system Administrators are definable per Administrator.
4)	Administrator actions/capabilities range from basic system monitoring to control of all system functions.
5)	Administrators can be linked and managed by LDAP systems.
d.	System Programming:
1)	User-friendly, intuitive, and responsive HTML5 web client interface.
2)	Single Page Application (SPA) architecture allows seamless browser transition between pages.
3)	Ability to import large quantities of cards in a CSV file format. 
e.	Alert messages:
1)	Ability to monitor for specific events and make them spawn additional windows or email the event to the administrator
2)	Alert information displayed in text format on the notifications area, and highlighted based on severity of alert.
3)	Video feed switching capabilities associated with alert via IP communication. (fully configurable)
4)	Capability of E-Mailing alert events to administrators.
f.	System integration:
1)	VMS integration:
a.	ViconNet® Digital Video Management system
b.	Digital Watchdog® DW Spectrum
c.	exacq® exacqVision
d.	Milestone® Xprotect
2)	Microsoft Active Directory Integration via LDAP protocol
3)	CardPresso Photo badging software integration. 
4)	Alarm system integration via configurable dry contact output/input.
5)	ASSA ABLOY Aperio hub integration 

B.	System Minimum Requirements:
Specifier Note: The computer specifications are the minimum standards for a basic system. When a system includes a large number of clients, controllers, and/or users, additional server power is strongly recommended.
1.	Central Processing Unit Computer:
a.	Microsoft compatible Windows 7 or newer.
b.	2GHz or faster 32-bit (x86) or 64-bit (x64) processor. Two or more cores.
c.	4GB RAM for 32-bit and 6GB RAM for 64-bit
d.	DVI or HDMI monitor
e.	1GB hard drive space required (Additional space required for database).
f.	Microsoft .Net Framework 4.5 Full.
g.	Microsoft SQL Server 2008 or SQL Server 2008 Express or Higher.

Specifier Note: Article below includes submittal of relevant data to be furnished by Contractor before, during or after construction. Coordinate this article with Architect’s and Contractor’s duties and responsibilities in Conditions of the Contract and Section 01 33 00 - Submittal Procedures.
1.4	SUBMITTALS
A.	General: Submit listed submittals in accordance with Conditions of the Contract and Section [01 33 00 - Submittal Procedures] [_____].
B.	Product Data: Submit product data for specified products, ____ copies
C.	Manufacturer’s Instructions: Manufacturer’s Technical installation guide, and Manufacturer’s Software Guide, ____copies.
D.	Drawings: Submit shop drawings detailing installation procedures, including layout, dimensions and support placement, ___ copies.
Specifier Note: Coordinate paragraph below with Part 3 Field Quality Requirements Article. Retain or delete as applicable.
E.	Closeout Submittals: Submit the following:
1.	Warranty: Warranty documents.
2.	Operation and Maintenance Data: Operation and maintenance data for installed products in accordance with Section [01 78 00 - Closeout Submittals] [_____]. Include methods for maintaining installed products and precautions against cleaning materials and methods detrimental to finishes and performance.

1.5	QUALITY ASSURANCE
A.	Qualifications:
1.	Installer:  Experienced in performing work of this section, and having specialized knowledge in installation of systems similar to that required for this project. Installer must be a manufacturer trained and authorized Vicon installer, providing termination, commissioning and end-user training (technical and/or administrative) services as required.

2.	Manufacturer: Capable of providing field service representation during construction, and approving installation and application method, as well as providing termination, commissioning and end user training (technical and/or administrative) services as required. 
Specifier Note: Paragraph below should list obligations for compliance with specific code requirements particular to this section. General statements to comply with a particular code are typically addressed in Conditions of the Contract and Section 01 41 00 - Regulatory Requirements. Repetitive statements should be avoided. 
B.	Regulatory Requirements: In accordance with Section [01 41 00 - Regulatory Requirements] [_____]. 
1.	IEEE 1100.
2.	NFPA 70.
3.	NFPA 72.
4.	NFPA 80.
5.	NFPA 101.
C.	Pre-installation Meetings: Conduct pre-installation meeting to verify project requirements, manufacturer’s installation instructions and manufacturer’s warranty requirements. Comply with [Section 01 31 19 - Project Meetings].

1.6	DELIVERY, STORAGE & HANDLING
A.	General: Comply with Section [01 61 00 - Common Product Requirements].
B.	Ordering: Comply with manufacturer’s ordering instructions and lead time requirements to avoid construction delays.
C.	Delivery: Deliver materials in manufacturer’s original, unopened, undamaged containers with identification labels intact.
D.	Storage and Protection: Store materials indoors, protected from exposure to harmful weather conditions and at a temperature between 10 and 30 degrees Celsius, and between 10% and 90% relative humidity, non-condensing. Product boxes not to be stacked more than 3 high, and are not to have anything stacked on top or directly beside the product that could possibly cause damage based on weight, moisture, corrosive content etc.   
Specifier Note: Coordinate article below with Conditions of the Contract and with Division 01 Closeout Submittals (Warranty) Section.
1.7	WARRANTY
A.	Project Warranty: Refer to Conditions of the Contract for project warranty provisions. Submit, for Owner’s acceptance, manufacturer’s standard warranty document executed by authorized company official. Manufacturer’s warranty is in addition to, and not a limitation of, other rights Owner may have under Contract Documents. 

B.	Manufacturer’s Warranty: Vicon Industries warrants all Vicon Access Control Controllers made for Vicon are free from defects in material and workmanship. However this warranty does not cover non-manufactured peripheral products sold by Vicon. Peripheral products are covered by the manufacturer’s warranty of the particular peripheral device.

C.	Warranty Period: Vicon Controllers carry a 3 (three) year warranty from date of substantial completion. Vicon Industries will repair or replace defective equipment upon return to its facility, if they find that the warranty was breached in any way, Vicon Industries will not warrant any damage that occurred during shipping or handling, or damage caused by a repair or an attempt to repair by any person other than those authorized by Vicon Industries. This warranty covers normal industrial use and does not cover defects or damage to any product which, in the sole opinion of Vicon Industries has been subject to improper installation, unauthorized modification, misuse, neglect, abuse, or abnormal operating conditions, improper storage, or which has been attributable to acts of God such as lighting. Installation, which is not in accordance with the installation instructions, published by Vicon Industries, will void the warranty. This warranty does not cover defects or damage caused by a product, which is not approved by Vicon Industries and is connected to a Vicon Access Control system.

The said warranty only applies to the original purchaser and is and shall be in lieu of any and all other warranties. 
** Please note this does not include shipping, which will be supplied by the customer.

PART 2	- PRODUCTS
Specifier Note: Retain article below for proprietary method specification. Add product attributes performance characteristics, material standards and descriptions as applicable. Use of such phrases as “or equal” or “or approved equal” or similar phrases may cause ambiguity in specifications. Such phrases require verification (procedural, legal and regulatory) and assignment of responsibility for determining “or equal” products.
2.1	ELECTRONIC ACCESS CONTROL MANAGEMENT SYSTEM
A.	The product manufacturer shall be: VICON INDUSTRIES, INC.
1.	Contact: ADDRESS 135 Fell Court, Hauppauge, NY 11788
PHONE 631-952-2288, FAX 631-951-2288.
WEBSITE http://www.vicon-security.com
B.	The following components shall be available for system operation:
1.	One Door Controller: VAX-1D-REX/VAX-1D
a.	Supports 2 readers (IN and OUT configuration)
b.	Power input: IEEE 802.3af PoE standard provides up to 15.4 Watts.
c.	Processor: 32-Bit Microprocessor-Based
d.	Storage: 100,000 users, 50,000 events (onboard).
e.	Terminals: Quick disconnect terminal headers. 
f.	Reader Communications: Wiegand Data1/Data0.
g.	Lock Power: Solid State 12VDC @ 500mA / 24 VDC  @ 250 mA (with opt. converter)
h.	Auxiliary Power: 12VDC @ 200mA max. (Used to power motion devices, Piezo’s, etc.) 
Not to be used to power Magnetic locks or Electric strikes. 
i.	Reader power:  12VDC @ 250mA max. per port
j.	Relay Outputs: SSR Relay2, SSR Relay3 - 60V (TVS circuit limits 24V), 500mA, fully configurable, no mechanical ports.
k.	Reader Formats: Magnetic stripe, Biometric, Bar code, and Wiegand 40, 37, 36, 35, 32 & 26 bit. 
l.	Inputs: 4 Dry contact inputs, fully configurable including supervised or digital input setting (includes door contact, exit button, external request to exit (REX model), motion, etc.).
m.	Networking: 10/100Mbps supporting Static or DHCP modes with 2 Ethernet status LEDs; 256 bit
  AES encryption between panel and server (optional).
n.	Tamper Sensor: Photo tamper sensor (configurable) (no moving parts).
o.	LED Indicator: 2 PoE power indicator, 2 Reader active indicators, 3 output indicators, 1 communication status and Door status and heartbeat LED beneath unit.
p.	2 Line x 16 Ch LCD Display (contrast adjustable) with LED back light (brightness adjustable) used for on-board diagnostics and initial configuration such as IP address and communication modes.
q.	Keyboard: Four user push buttons for data entry or output selection.
r.	Sound: On-board piezo buzzer (90dB at 10cm).
s.	Motion (optional): PIR motion sensor mounted on bottom of unit for authorizing exit without card 
 read.
t.	Time: Keeps up to 1 month without power connection, No battery needed. Automatic DST switch.
u.	Operating Temperature: 0 degrees Celsius to 50 degrees Celsius 
 (32 degrees Fahrenheit to 122 degrees Fahrenheit).
v.	Operating Humidity: 10% to 90% relative humidity, non-condensing.
w.	Expandable modular design.
x.	PCB Dimensions: 7.4cm X 19.6cm (7.716” X 2.913”).
y.	Enclosure Dimensions: 28.6cm (W) X 38.75cm (H) X 7.7cm (D) (11.25”X15.25”X3”).
z.	Enclosure Color: Black or White.
aa.	Compliance: Panel is ETL Listed conforms to UL 294 Certified to CSA-C22.2 no.205. 

2.	Two Door Controller: VAX-2D-REX/VAX-2D
a.	Supports 2 readers (1 for each door)
b.	Power input: IEEE 802.3af PoE standard provides up to 15.4 Watts.
c.	Processor: 32-Bit Microprocessor-Based.
d.	Storage: 100,000 users, 50,000 events (onboard).
e.	Terminals: Quick disconnect terminal headers. 
f.	Reader Communications: Wiegand Data1/Data0.
g.	Lock Power 1: Solid State 12VDC @ 500mA / 24 VDC  @ 250 mA (with opt. Converter)
h.	Lock Power 2: SSR Relay2, - 60V (TVS circuit limits 24V), 500mA, fully configurable, no mechanical ports requires external lock power for second strike.
i.	Auxiliary Power: 12VDC @ 200mA max. (Used to power motion devices, Piezos, etc.) 
Not to be used to power Magnetic locks or Electric strikes. 
j.	Reader power:  12VDC @ 250mA max. per port
k.	Relay Outputs:  SSR Relay3 - 60V (TVS circuit limits 24V), 500mA, fully configurable, no mechanical ports.
l.	Reader Formats: Magnetic stripe, Biometric, Bar code, and Wiegand 40, 37, 36, 35, 32 & 26 bit. 
m.	Inputs: 4 Dry contact inputs, fully configurable including supervised or digital input setting (includes door contact, exit button, external request to exit (REX model), motion, etc.).
n.	Networking: 10/100Mbps supporting Static or DHCP modes with 2 Ethernet status LEDs; 256 bit AES encryption between panel and server (optional).
o.	Tamper Sensor: Photo tamper sensor (configurable) (no moving parts).
p.	LED Indicator: 2 PoE power indicator, 2 Reader active indicators, 3 output indicators, 1 communication status and Door status and heartbeat LED beneath unit.
q.	2 Line x 16 Ch LCD Display (contrast adjustable) with LED back light (brightness adjustable) used for on-board diagnostics and initial configuration such as IP address and communication modes.
r.	Keyboard: Four user push buttons for data entry or output selection.
s.	Sound: On-board piezo buzzer (90dB at 10cm).
t.	Motion (optional): PIR motion sensor mounted on bottom of unit for authorizing exit without card read.
u.	Time: Keeps up to 1 month without power connection, No battery needed. Automatic DST switch.
v.	Operating Temperature: 0 degrees Celsius to 50 degrees Celsius 
(32 degrees Fahrenheit to 122 degrees Fahrenheit).
w.	Operating Humidity: 10% to 90% relative humidity, non-condensing.
x.	Expandable modular design.
y.	PCB Dimensions: 7.4cm X 19.6cm (7.716” X 2.913”).
z.	Enclosure Dimensions: 28.6cm (W) X 38.75cm (H) X 7.7cm (D) (11.25”X15.25”X3”).
aa.	Enclosure Color: Black or White.
bb.	Compliance: Panel is ETL Listed conforms to UL 294 Certified to CSA-C22.2 no.205. 

3.	Elevator Master Panel:  VAX-ELV-STR 
a.	Supports 2 Readers (1 per cab)
b.	Power input: IEEE 802.3af PoE(Power over Ethernet) standard(15.4W) or PoE+ power
c.	Processor: Processor: 32-bit microprocessor
d.	Storage: 50,000 users, 50,000 events (on board).
e.	Terminals: Quick disconnect terminal headers. 
f.	Reader Communications: Wiegand Data1/Data0.
g.	Auxiliary Power: 12VDC @ 200mA max. (Used to power Elevator Expander Boards) 
h.	Reader power:  12VDC @ 250mA max. per port
i.	Reader Formats: Magnetic stripe, Biometric, Bar code, and Wiegand 40, 37, 36, 35, 32 & 26 bit
j.	Communications: On board RS485 via RS-485 module SE-X02 up to 8 Elevator Expander Board.
k.	Networking: 10/100Mbps supporting Static or DHCP modes with 2 Ethernet status LEDs; 256 bit AES encryption between panel and server (optional).
l.	Tamper Sensor: Photo tamper sensor (configurable) (no moving parts).
m.	LED Indicator: 2 PoE power indicator, 2 Reader active indicators, 1 communication status, heartbeat LED beneath unit.
n.	2 Line x 16 Ch LCD Display (contrast adjustable) with LED back light (brightness adjustable) used for on-board diagnostics and initial configuration such as IP address and communication modes.
o.	Keyboard: Four user push buttons for data entry or output selection.
p.	Sound: On-board piezo buzzer (90dB at 10cm).
q.	Time: Keeps up to 1 month without power connection, No battery needed. Automatic DST switch.
r.	Elevators:
1)	Ability to support up to 4 Cabs per master panel.
2)	Ability to support up to 64 Floors per master panel (with 8 Expander Boards)
3)	Up to 2 readers.
4)	Ability to support Button Sensing or Non-Button Sensing.
s.	Elevator Time Zones:
1)	User:
a)	Ability to support 256 user time zones: 4 zones (9 boundaries) per day.
b)	Ability to support  50 user holiday time zone groups, each has 50 holidays, each user holiday time zone : 2 zones (5 boundaries) per day
2)	Floor:
a)	Ability to support 64 (unlimited) floor time zones, 4 zones (9 boundaries) per day.
b)	Ability to support 8 floor holiday time zone groups, each has 50 holidays, each floor holiday time zone: 2 zones (5 boundaries) per day.
c)	Ability to support 64 one time run time zones (ad-hoc).
t.	Operating Temperature: 0 degrees Celsius to 50 degrees Celsius 
(32 degrees Fahrenheit to 122 degrees Fahrenheit).
u.	Expandable modular design.
v.	PCB Dimensions: 7.4cm X 19.6cm (7.716” X 2.913”)
w.	Enclosure Dimensions: 28.6cm (W) X 38.75cm (H) X 7.7cm (D) (11.25”X15.25”X3”).
x.	Enclosure Color: Black or White or Blue can
y.	Compliance: Panel is ETL Listed conforms to UL 294 Certified to CSA-C22.2 no.205. 

4.	Elevator Expander Board:  VAX-IO-EXP8
a.	Processor: Processor: 32-bit microprocessor
b.	Power input: 12VDC supplied by Elevator Master Panel, no external power needed.
c.	Configuration: 8 Dip switches for inputting addressing and diagnostics. 
d.	Communication: RS-485 (2-wire communication) Multidrop (Daisy Chain or Star) via SE-EX02 Module.
e.	Inputs: 8 dry contact inputs. Fully configurable. 
f.	 Outputs: 8 dry contact SSR Relays. Fully configurable.
g.	Terminals: Quick disconnect terminal headers. 
h.	PCB Dimensions: 9.5cm X 9.5cm (3.740” X 3.740“)

5.	IO-Master Panel: Included with VAX-IO-STR
a.	Power input: IEEE 802.3af PoE(Power over Ethernet) standard(15.4W) or PoE+ power
b.	Processor: Processor: 32-bit microprocessor
c.	Storage:
1.	50,000 events (on board)
d.	Terminals: Quick disconnect terminal headers.
e.	Auxiliary Power: 12VDC @ 450mA. (Used to power PRS-IO8 Board IO/Elevator expander board) Current shared with two reader ports.
f.	Communications: On board RS485 via RS-485 module SE-X02 to up to 8 IO Expander Boards.
g.	Networking:
1.	10/100Mbps supporting Static or DHCP modes with 2 Ethernet status LEDs; 256 bit AES encryption between panel and server (optional).
2.	LED Indicator: 2 x PoE power indicator
h.	Security: Hardware secured by configurable password.
i.	Tamper Sensor: Photo tamper sensor (configurable) (no moving parts).
j.	Display:
1.	2 Line x 16 Character LCD Display with LED back light used for on-board diagnostics and initial configuration such as IP address and communication modes.
2.	Contrast adjustable.
3.	Brightness adjustable.
k.	Keyboard: Four user push buttons for data entry or output selection.
l.	Sound: On-board piezo buzzer (90dB at 10cm).
m.	Diagnostics: Several on board diagnostics available including the following:
1.	Ping with IP:
a.	Ability to perform a basic network connectivity test by communicating with the server IP via ICMP protocol.
2.	Ping with Name:
a.	Ability to perform a basic network connectivity test by communicating to the server by resolving the name of the server via a Dynamic Name Service (DNS).
3.	Debug mode:
a.	Optional debug mode that allows extra logging of communications and panel decisions.
4.	Read Only mode: Displays controller configuration and miscellaneous information
a.	Panel Name
b.	Panel ID
c.	IP Address
d.	Panel MAC Address
e.	Panel Subnet Mask
f.	Panel Gateway
g.	Panel DNS
h.	Communication mode
i.	Server IP Address/Name
j.	Server Port
k.	Firmware Version
l.	Network Name
m.	DHCP Bound address
n.	Time (UTC and Local)
o.	Connection Status
n.	On-board Communication Configuration:
1.	Ability to configure communication method to server (name or IP address).
2.	Ability to configure name or IP address that the server can be reached.
3.	Ability to configure network settings of controller, including:
a.	Static IP address or DHCP
b.	Controller IP Address, subnet mask, default gateway, DNS server.
o.	Time: Keeps up to 1 month without power connection, No battery needed. Automatic DST switch.
p.	Firmware: Controller firmware is remotely upgradable from server software for added functionality, features and patches.
q.	IO-Boards:
1.	Ability to support up to to 64 Inputs and Outputs per master panel (with 8 Expander Boards)
r.	Input/Output Time Zones:
1.	Input:
a.	Ability to support 16 Input time zones: 2 zones (5 boundaries) per day.
b.	Ability to support 16 holiday groups, each has 50 holidays, each Input holiday time zone: 2 zones (5 boundaries) per day
2.	Output:
a.	Ability to support 64 Output time zones, 5 zones (11 boundaries) per day.
b.	Ability to support 8 holiday groups, each has 50 holidays, each Output holiday time zone: 2 zones (5 boundaries) per day.
s.	Input/Output Functions:
1.	Ability to place an Input on a schedule
2.	Ability to assign an Input to a holiday group
3.	Ability to place a detection time on an Input
4.	Ability to assign an action to an Input
5.	Input Actions:
a.	Do Nothing
b.	Activate Selected Output
c.	Deactivate Selected Output
d.	Toggle Selected Output
e.	Pulse Selected Output (high)
f.	Pulse Selected Output (low)
g.	Pulse Selected Output (opposite)
h.	Activate Multiple Outputs (up to 5)
i.	Deactivate Multiple Outputs (up to 5)
j.	Toggle Multiple Outputs (up to 5)
6.	Ability to place a delay on any Input Actions
7.	Ability to place an action duration for pulses
8.	Ability to configure an Input as Normally Closed
9.	Ability to place an Output on a schedule
10.	Ability to assign an Output to a holiday group
11.	Ability to configure an Output as Normally Closed
12.	Ability to configure an Output to not generate any events
13.	Ability to protect an Output from Input Actions
14.	Ability to configure an Output to be initially On
t.	Operating Temperature: 0 degrees Celsius to 50 degrees Celsius.
u.	Expandable modular design.
v.	PCB Dimensions: 19.6 cm (W) X 7.4cm (H) (7.716” X 2.913”).
w.	Enclosure Dimensions: 21.6cm (W) X 26.0cm (H) x 8.30cm (8.5" x 10.25" x 3.25").
x.	Enclosure Color: Blue can
6.	Elevator/IO Expander Board: VAX-IO-EXP8 Board/ VAX-IO-EXP16 Board
a.	Processor: Processor: 32-bit microprocessor
b.	Power Input: 12VDC supplied by Elevator/IO Master Panel, no external power needed.
c.	Configuration: 8/16 DIP switches for inputting addressing and diagnostics.
d.	Communication: RS-485 (2-wire communication) Multidrop (Daisy Chain or Star) via SE-EX02 Module.
e.	Inputs:
1.	8/16 x dry contact inputs. Fully configurable.
2.	LED Indicator: 1 x Input activity indicator.
f.	Outputs:
1.	8/16 dry contact Solid State Relays. Fully configurable.
2.	Capable of switching up to 60V, 500mA limit. Other relay options available.
3.	LED Indicator: 8/16 x output status indicator.
4.	Field replaceable solid state relays.
g.	Tamper: Each IO panel has individual photo-tamper sensor. Fully configurable.
h.	Diagnostics: Input/Output test mode, activated through DIP switch configuration.
i.	Terminals: Quick disconnect terminal headers.
B.	 IO-Board management to allow:
1.	Inputs:
a.	Ability to apply a name to each Input.
b.	Ability to define a detection time until the input is considered active.
c.	Ability to place an Input on a schedule to only monitor during specific times.
d.	Ability to apply holiday schedules to an input for alternate schedules during holidays.
e.	Ability to assign an action to be performed when the input is activated.
f.	Actions:
1.	Do Nothing
2.	Activate Selected Output
3.	Deactivate Selected Output
4.	Toggle Selected Output
5.	Pulse Selected Output (high)
6.	Pulse Selected Output (low)
7.	Pulse Selected Output (opposite)
8.	Activate Multiple Outputs (up to 5)
9.	Deactivate Multiple Outputs (up to 5)
10.	Toggle Multiple Outputs (up to 5)
g.	Ability to place a delay on any Input Actions.
h.	Ability to place an action duration for pulses.
i.	Ability to configure an Input as Normally Closed.
2.	Outputs:
a.	Ability to apply a name to each Output
b.	Ability to place an Output on a schedule
c.	Ability to apply holiday schedules to an Output for alternate schedules during holidays.
d.	Ability to configure an Output as Normally Closed.
e.	Ability to configure an Output to not generate any events.
f.	Ability to protect an Output from Input Actions.
g.	Ability to configure an Output to be initially On.

7.	Communication Converter: RS-485 module 
a.	LED Indicators: 1 Data Receive, 1 Data Send
b.	Terminals: Quick disconnect terminals, connects to expander module on ELEVATOR-64 Master Panel or APERIO-(2, 4, 8).
c.	Power Requirement: No external power needed.
d.	Communication: Capable of communicating to Elevator Expander Boards, ASSA ABLOY Aperio hub, or Input/Output Expander Board via RS-485 Bus.
e.	Warranty: 2 year, Limited.

8.	Mullion Mount Proximity Access Reader: 
a.	Dimensions:  4.5 x 1.6 x 0.75 inches (114 x 38 x 19mm)
b.	Design: Weatherproof.
c.	Characteristics: High reliability; consistent read range characteristics; low power consumption; vandal-resistant.
d.	Colors: Available in Black
e.	Features: Multicolor LED indicator-Red, Green, Amber, and Off.
f.	Mounting: Mullion, can be mounted directly to metal.
g.	Communication format: High security 40 bit, AWID, HID
h.	Frequency: 125 Khz excitation 
i.	Read Range: 3 inches - 6 inches (76mm - 152 mm) depending on credential.
j.	Operating Temperature: -40°F to +149°F (-40° C to +65° C)
k.	Current Draw: 5mA minimum, 45mA typical, 80mA peak.
l.	Compliance: CSA, UL, FCC, CE, C-Tick.
m.	Warranty: Limited Lifetime (as per manufacturer).

9.	High Security Vandal Proof Proximity Mullion Access Reader: 
a.	Dimensions: 5.25 x 2 x 0.75 inches (134x51x19 mm). 
b.	Design: Weatherproof, Vandal proof.
c.	Characteristics: High reliability; consistent read range characteristics; low power consumption; vandal-proof.
d.	Colors: Stainless Steel and Fibertex.
e.	LED: None
f.	Mounting: mullion may be mounted directly to metal.
g.	Communication format: High security 40 bit, AWID, HID
h.	Frequency: 125 Khz excitation 
i.	Read Range: up to 1 inch (25 mm).
j.	Operating Temperature: -40 to +65 degrees Celsius.
k.	Current Draw: 90mA typical.
l.	Compliance: CSA, UL, FCC, CE, C-Tick.
m.	Warranty: Limited Lifetime (as per manufacturer).

10.	Keypad/Proximity Access Reader: 
a.	Dimensions: 4.6 x 3 x 0.7 inches (117x77x18 mm). 
b.	Design: Weatherproof.
c.	Characteristics: Uses non-mechanical capacitive technology (no moving parts), High reliability; consistent read range characteristics; low power consumption; vandal-resistant.
d.	Colors: Available with Black or Off White cover.
e.	Features: Multicolor LED indicator-Red, Green, Amber, and Off.
f.	Mounting: Wall-single gang box, or may be mounted directly to metal. 
g.	Communication format: High security 40 bit, AWID, HID
h.	Frequency: 125 KHz excitation 
i.	Read Range: 3 inches – 6 inches (76 – 152 mm) depending on credential.
j.	Operating Temperature: -40 to +65 degrees Celsius.
k.	Current Draw: 30mA minimum, 50mA typical, 115mA peak.
l.	Compliance: FCC, CE, C-Tick.
m.	Warranty: Limited Lifetime (as per manufacturer).

11.	Long Range Single Gang Access Reader: 
a.	Dimensions: 8.6 x 6 x 1 inches (216x152.4x25.4 mm). 
b.	Design: Weatherproof.
c.	Characteristics: High reliability; consistent read range characteristics; low power consumption; vandal-resistant.
d.	Colors: Black
e.	Features: Multicolor LED indicator-Red, Green, Amber, and Off.
f.	Mounting: Wall-single gang box, or non-metallic flat surfaces. 
g.	Communication format: High security 40 bit, AWID, HID.
h.	Frequency: 125 KHz excitation 
i.	Read Range: Up to 15 inches (up to 381 mm) depending on credential.
j.	Operating Temperature: -40 to +65 degrees Celsius.
k.	Current Draw: 200mA typical, 600mA peak.
l.	Compliance: FCC, CE, C-Tick, ICC.
m.	Warranty: Limited Lifetime (as per manufacturer).

12.	Long Range Single Gang Access Reader: 
a.	Dimensions: 10.5 x 10.5 x 2.0 inches (267 x 267 x 53 mm) 
b.	Design: Weatherproof.
c.	Characteristics: High reliability; consistent read range characteristics; low power consumption; vandal-resistant.
d.	Colors: Black
e.	Features: Multicolor LED indicator-Red, Green, Amber, and Off.
f.	Mounting: US- size metal or plastic single or double gang wall box, standard parking bollard X-mounts or non-metallic flat surfaces.
g.	Communication format: High security 40 bit, AWID, HID.
h.	Frequency: 125 KHz excitation 
i.	Read Range: Up to 20 inches (up to 508 mm) depending on credential.
j.	Operating Temperature: -40 to +65 degrees Celsius.
k.	Current Draw: 200mA typical, 600mA peak.
l.	Compliance: FCC, CE, C-Tick, ICC.
m.	Warranty: Limited Lifetime (as per manufacturer).

13.	Graphic Quality Proximity Card: 
a.	Size: 3.4x2.2x0.06 inches (86x55x1.5 mm).
b.	Printing Surface Imaging: Use PVC9 Glossy Adhesive Overlay for color dye sublimation printing of images and text.
c.	Frequency: 125 kHz excitation. 
d.	Communication format: High security 40 bit. 
e.	Operating Temperature: -40 to +65 degrees Celsius.
f.	Slot Punch: Vertical
g.	Compliance: CSA, UL, FCC, CE, C-Tick.
h.	Warranty:  Limited Lifetime warranty as per Manufacturer.  

14.	Image technology Proximity Card: 
a.	Size: 3.38x2.12x0.0.046 inches (85.9x53.8x1.17 mm).
b.	Printing Surface Imaging: Appropriate for direct color dye sublimation printing of images and text.
c.	Frequency: 125 kHz excitation.
d.	Communication format: High security 40 bit.
e.	Operating Temperature: -40 to +65 degrees Celsius.
f.	Slot Punch: Required
g.	Compliance: CSA, UL, FCC, CE, C-Tick.
h.	Warranty:  Limited Lifetime warranty as per Manufacturer.  

15.	Proximity Key Tag: 
a.	Dimensions: 1.5x1.2x0.15 inches (36x29x3.8 mm).
b.	Color: Light Grey
c.	Operating Temperature: -40 to +65 degrees Celsius.
d.	Features: Reinforced Brass eyelet easily fits on key ring.
e.	Communication format: High security 40 bit. 
f.	Warranty:  Limited Lifetime warranty as per Manufacturer.  

16.	Long Range Wireless RF Receiver: 
a.	Dimensions: 6.3 x 3.3 x 2.3 inches (160x86.4x58.4 mm). 
b.	Design: Weatherproof
c.	Characteristics: High reliability, long read range, encrypted rolling code transmission.
d.	Colors: Off White 
e.	Features: Multicolor LED indicator-Red, Green, and Off.
f.	Mounting: Wall-single gang box, or non-metallic flat surfaces.
g.	Read Range: 4 inches - 8inches (102 – 203 mm) depending on credential.
h.	Operating Temperature: -40 to +65 degrees Celsius.
i.	Current Draw: 80mA typical.
j.	Compliance: FCC, IC, CE, C-Tick.
k.	Warranty: Limited 1 year (as per manufacturer).

17.	 Combination One Button Wireless RF Transmitter and Proximity Credential: 
a.	Dimensions: 2.3 x 1.3 x 0.4 inches (58.4x33x10.2 mm).
b.	Design: Weatherproof
c.	Characteristics: High reliability, long read range, rolling code + encrypted algorithm for secure transmission.
d.	Communication format: High security 40 bit.
e.	Colors: Black 
f.	LED: Red LED standard (activated upon button press).
g.	Read Range:
1)	Button press up to 150ft (46m) with HC-HARWRR-42 Receiver
2)	Proximity presentation up to 2 inches (51mm)
h.	Operating Temperature: -25 to +50 degrees Celsius.
i.	Battery: 27A, NM27 size 12V Alkaline.
j.	Compliance: FCC, IC, CE, C-Tick.
k.	Warranty: Limited 1 year (as per manufacturer).

18.	Combination Four Button Wireless RF Transmitter and Proximity Credential: 
a.	Dimensions: 2.3 x 1.3 x 0.4 inches (58.4x33x10.2 mm).
b.	Design: Weatherproof.
c.	Characteristics: High reliability, long read range, rolling code + encrypted algorithm for secure transmission.
d.	Communication format: High security 40 bit. 
e.	Colors: Black 
f.	LED: Red LED standard (activated upon button press).
g.	Read Range:
1)	Button press up to 150ft (46m) with Receiver
2)	Proximity presentation up to 2 inches (51mm)
h.	Operating Temperature: -25 to +50 degrees Celsius.
i.	Battery: 27A, NM27 size 12V Alkaline
j.	Compliance: FCC, IC, CE, C-Tick
k.	Warranty: Limited 1 year (as per manufacturer).

2.2	SOFTWARE FEATURES AND FUNCTIONS
Specifier Note: The access control software modules consist of many functions and they need to be specified here. These software modules are required to activate the system component functions. A software license is NOT required to activate these software features and functions. 

A.	Server Software:
1.	Shall be installed on a standard PC running Microsoft Windows 7 Home or Higher (Windows 7 Starter Not Supported) or purchased via an embedded hardware server box.
2.	Shall support Microsoft SQL Server 2008, SQL Server 2008 Express, or later version.
3.	Shall be 100% web based and can be accessed via any web enabled device including Cell Phones, Tablets, Laptops, PCs with any operating system etc. without the need for any additional plug in’s (i.e. no active x controls, Flash, etc.).
4.	Software design shall be of a Web REST API allowing full integration to third party software or a custom front end.
5.	Software design shall be of a Single Page Application (SPA) architecture allowing seamless navigation between screens.
6.	Shall have Responsive Web Design (responsive views automatically adjust based on device size)
7.	Shall have ability to Partition software for multisite all hosted from one location allowing site administrators only access to their site readers and cards or multiple sites
8.	Shall have functions that will be accessed via tool bar Icons, including Help prompts that will appear when the mouse pointer hovers over the selection button.
9.	Shall be possible to install the server software in a virtualized environment.

B.	Administrator Control Capabilities:
1.	Shall provide an Administrator interface secured by encrypted password control and SSL communication from web client to server.
2.	Shall provide for an Administrator that can either be a System-Admin or a Non-sys-admin with customizable permissions.
3.	Shall support Administrator Management which determines privileges, functions, and Partitions that can be accessed. Functions that cannot be accessed will not be visible. The following items are available:
a.	Manage Access Privilege Groups 
b.	Manage Cameras And Integration 
c.	Manage Door Holiday Groups 
d.	Manage Door Holiday TimeZones 
e.	Manage Door TimeZones 
f.	Manage Doors 
g.	Manage Elevators 
h.	Manage Floor Holiday Groups 
i.	Manage Floor Holiday TimeZones 
j.	Manage Floor TimeZones 
k.	Manage Holidays 
l.	Manage OneTimeRun TimeZones 
m.	Manage Panels 
n.	Manage Sites 
o.	Manage User Holiday Groups 
p.	Manage User Holiday TimeZones 
q.	Manage User TimeZones 
r.	Manage Users 
s.	Reporting Reporting Alerts 
t.	Reporting DoorActivity 
u.	Reporting FloorActivity 
v.	Reporting UserActivity 
w.	Reporting UserList 
x.	Special Permissions Override Door 
y.	Override Floor 
z.	Override Output 
aa.	Update Panel 
bb.	View Cameras 
cc.	View Status 

C.	System Partitioning:
1.	System shall support unlimited partitions (with appropriate licensing), which logically separate the system into pieces.
2.	Administrators can be given permissions to manage specific aspects of a partition or multiple partitions.
3.	Administrators shall only see partitions or parts of partitions they are explicitly given permission to manage.
4.	Ability to assign user/cardholders to more than 1 partition, as long as the Administrator assigning access groups has permissions to manage cardholders within the desired partitions.
5.	Administrators with limited permissions will not see the menus/icons for parts of the software they do not have permission to use.
6.	Door and Elevator Panels shall be assigned to a single partition.
7.	Holidays, schedules and Access groups shall not be shared between partitions.
8.	Administrator shall not see events on devices they do not have permission to view/manage.

D.	Credential/Cardholder Management:
1.	Shall provide User/Cardholder management screen with unlimited number of users/cardholders (100,000 per controller).
2.	Shall provide Simple cardholder enrollment, with all available cardholder options available on one screen.
3.	Shall support assignment of Unlimited credentials to a single cardholder, including Cards, Pins, biometrics, etc.
4.	Shall support assignment of additional user/cardholder attributes.
a.	Assign a Start/Stop date to a cardholder.
b.	Assign a security level for Crisis Level feature.
c.	Assign the cardholder as a Master user.
d.	Assign the cardholder as a Supervisor user.
e.	Assign the cardholder the permission to activate First Person In schedules.
f.	Assign the cardholder the ability to perform Triple Swipe Actions.
g.	Assign the cardholder the ability to disarm an external alarm system.
h.	Assign the cardholder the ability to open auto-openers without the use of a button.
5.	Shall provide ability to view a list of all cardholders.
6.	Shall provide capability of finding a specific card holder based on specified search criteria such as name or credentials.
7.	Shall provide the ability to assign a photographic image for each Cardholder, image can be uploaded from local device or taken in the web browser with an image device. (Chrome only).
8.	Shall provide ability to assign to Unlimited Access Privilege Groups.
9.	Shall provide ability to assign cardholder to Access Privilege Groups across different Partitions.
10.	Shall provide ability to assign cardholder directly to a Partition for later access assignment.
11.	Shall provide ability to assign Unlimited custom fields to a cardholder.
12.	Shall provide ability to import large amounts of users/cardholders via CSV file.
 
E.	Access Privilege Groups:
1.	Shall support ability to create unlimited administrator definable/customizable Access Privilege Groups.
2.	Shall support ability to apply any combination of door/time zone.  
3.	Shall support restriction/allowance of Cardholders movement through identified doors, at specific times, including holiday schedule.

F.	Time Zone Management:
1.	The system shall have separate sections for time zones for user access (User Time Zones), door access (Door Times Zones), as well as floor access (Floor Time Zones).
2.	The system time zones shall be drag and drop graphics allowing for easy viewing, as well as eliminating the chance of programming error.
3.	The system time zones shall be color coded to the mode of the span for easy viewing and eliminating the chance of programming error.
4.	Shall have ability to provide a specific schedule name and description.
5.	Door Time Zones (door schedule):
a.	Shall support an Unlimited amount of Door Time Zones.
b.	Shall support 20 unlock/lock times per day.
c.	Shall support 8 different Time Zone modes in any combination:
1)	Ability to have Lockdown (no cards other than cards flagged as master will be granted access).
2)	Ability to have Card Only (valid cards required to grant access).
3)	Ability to have Pin Only (valid pins required to grant access).
4)	Ability to have Card or Pin (valid card or pin required for access).
5)	Ability to have Card and Pin (valid card and pin required for access).
6)	Ability to have Unlock (door is in public mode).
7)	Ability to have “First Credential in” by card (door will not follow its public schedule until a card flagged with first card in feature is presented at the door during the public schedule)
8)	Ability to have Dual Credentials (2 valid cards one flagged as supervisor required to grant access).
6.	User Time Zone (user access schedule):
a.	Shall support up to 256 User Time Zone schedules the system will support. 
b.	Shall support 8 Allowed/Not Allowed time spans per day.
c.	Shall support 2 different Time Zone modes in any combination:
1)	Ability to have Allowed (user will be allowed through the door as long as the Door Time Zone is in a mode that accepts the type of credential being presented).
2)	Ability to have Not Allowed (user will be denied access to the door).
7.	Floor Time Zones (elevator floor schedule):
a.	Ability shall support Unlimited Floor Time zone schedules the system will support.
b.	Ability shall have 8 time spans per day.
c.	Shall support 3 different Time Zone modes in any combination:
1)	Ability to have Card Only (valid cards required to grant access).
2)	Ability to have Unlock (floor is in public mode).
3)	Ability to have Lockdown (no cards other than cards flagged as master will be granted access).
G.	Holiday Management to Allow:
1.	Ability to apply a specific schedule for groups of doors to follow when it is a holiday.
2.	Ability to apply a specific user schedule for groups of users to follow during a holiday.
3.	Ability to create a holiday with the following options:
a.	Date of the holidays.
b.	If the holiday is reoccurring annually.
c.	Name and description of the holiday.
d.	Which groups of doors will be affected by the holiday and what holiday time zone they will follow.
e.	Which groups of Access Privilege Groups will be affected by the holiday and what holiday time zone they will follow.

H.	Door Management shall provide the following:
1.	Ability to apply a specific name and description to each door and reader.
2.	Ability to apply a time zone to control when a specific door is to unlock/lock, accept cards, pins, etc.
3.	Ability to apply a Holiday group to control how a specific door will behave on a Holiday.
4.	Ability to configure door held open alarms and door forced open alarms.
5.	Additional functions, including lock release time and door held open time.
6.	Ability to configure if a motion device can unlock the door.
7.	Ability to configure Automatic Opener options, including timers and unlock delay.
8.	Ability to configure back to back reader interference interval.
9.	Ability to configure Anti-passback options.
10.	Ability to configure Door Camera associations.

I.	Elevator management shall provide the following:
1.	Ability to manage up to 64 floors per elevator cab per Elevator Master Panel.
2.	Ability to apply a specific name and description to each cab, reader and floor
3.	Ability to manage up to 4 cab per Elevator Master Panel.
4.	Ability to configure if a cab is using button sensing.
5.	Ability to apply a time zone to control when a specific Floor is to unlock/lock, accept cards.
6.	Ability to apply a Holiday group to control how a specific floor will behave on a Holiday.

J.	Panel management shall provide the following:
1.	Ability to apply a specific name and description to each door/elevator panel.
2.	Ability to assign a panel to a specific partition.
3.	Ability to configure a password code for accessing the panel LCD interface and panel web interface.
4.	Ability to disable/enable the web interface of the panel for remotely configuring IP settings.
5.	Ability to configure the panel connection mode as static IP or DHCP.
6.	Ability to configure the LCD screen on the panel, brightness and on time.
7.	Ability to configure how long a forced open buzzer lasts.
8.	Ability to configure the panel tamper sensor sensitivity and disable/enable.
9.	Ability to configure how the integrated motion behaves, along with sensitivity options.
10.	Panel Inputs and outputs are 100% configurable, all inputs/outputs can be configured as normally open or normally closed, supervised, events enabled/disabled.
11.	Ability to configure Inputs as any of the following functions:
a.	Request to Exit.
b.	Door Contact.
c.	Door Opener to exit.
d.	Motion Sensor.
e.	Emergency alarm.
f.	External Alarm Status.
g.	Door Opener to Enter.
h.	Aux Input action:
1)	Toggle/Activate/Pulse selected output.
2)	Toggle/Activate/Pulse alarm interface.
3)	Override doors with Crisis Level.
4)	Play Sound.
12.	Ability to configure Outputs/Relays as any of the following functions:
a.	Door Strike.
b.	Door Opener.
c.	External Buzzer.
d.	Alarm Interface.
e.	Aux Output.
f.	Secondary Door Strike.

K.	Area Management shall provide the following:
1.	Labeling: Ability to name areas and sites
2.	Local Timed Anti-passback: Ability to control re-entry into an area, at a specific door, based on a definable time value.
3.	Reset: Allow the ability to reset the Anti-passback on a per panel basis.
4.	Ability to configure soft or hard Anti-passback.
5.	Ability to configure Anti-passback to ignore cardholders with the Supervisor flag.
6.	Ability to configure Anti-passback to ignore or take into consideration the opening of a door as a cardholder entering/exiting an area.

L.	System Partitioning shall provide the following:
1.	Unlimited Partitions, which logically separate the system into pieces.
2.	Administrators can be given permissions to view/change specific aspects of a Partition or multiple Partitions.
3.	Administrators can only see Partitions or parts of Partitions they are explicitly given permission to view/edit.
4.	User/cardholders can belong to more than 1 partition, as long as the Administrator assigning access groups has permissions to manage cardholders in both Partitions.
5.	Administrators with limited permissions will not see the menus/icons for parts of the software they do not have permission to use.

M.	Video Camera integration shall allow the following:
1.	Ability to be integrated with 1 or more of the following Video Management Software (VMS) systems
a. ViconNet® Digital Video Management system.
b. Digital Watchdog DW Spectrum
c. exacq exacqVision
d. Milestone XProtect
2.	Support to integrate with multiple instances of ViconNet® Digital Video Management system across
different communication mediums such as LAN/WAN.
3.	Real-time video monitoring displays, including unlimited cameras simultaneously.
4.	Associate unlimited cameras with a Door or Elevator.
5.	Associate a PTZ camera with a door based on a pre-defined position.
6.	Ability to configure specific events to spawn a Camera matrix right above the notifications/events area of the web interface.
7.	 Linking of video and events based on pre-defined events provided by the access control software.
8.	Historical events can spawn a video matrix to cameras.
9.	Administrator permissions specific to who can manage and make changes to the camera system.

N.	Alert Management shall provide the following: 
1.	Ability to display alert events with date and time, source and description on the notifications screen, color coded to the severity of the event. (Red, Blue or Green).
2.	Permit event type alert messages, such as access denied, door forced open, and door held open.
3.	Ability to configure specific event types to spawn camera matrix with cameras associated with the door/Elevator the event is associated with.
4.	Ability to configure e-mail alert messages to the administrator. Each administrator configures their own list of alerts that they are notified of via email.

O.	Microsoft Active Directory (AD) Integration via LDAP protocol:
1.	Ability to obtain read only directory information from LDAP provider.
2.	Ability to synchronize AD Users based on selected AD Security Groups.
3.	Ability to choose which AD Security Groups AD Users will be synchronized from. 
4.	Ability to configure AD Security Groups as Access Privilege Groups.
5.	Ability to give access to Doors/Floors based on AD Security Group membership.
6.	Ability to synchronize the following AD User information:
a.	First Name & Last Name
b.	User Expiry Date
1)	Expired Users will have access rights to Doors/Floors removed.
c.	User Status (enabled/disabled)
1)	Disabled Users will have access rights to Doors/Floors removed.
d.	AD Group membership
7.	Ability to synchronize credentials (Card/FOB/PIN) via AD User Attribute Fields.
8.	Ability to synchronize credentials in the following manners:
a.	Wiegand Credential from Single AD Attribute Field
b.	Wiegand Credential from 2 individual fields with Fixed Site Code
c.	Wiegand Credential from three Individual Fields
d.	PIN from single field
9.	Ability to synchronize AD User Attributes as Custom Fields.
10.	Ability to configure how often Protector.Net checks the LDAP provider for changes (1 to 60 minutes).
11.	Ability to automatically disable Users who have been deleted or disabled in Active Directory without panel update required.
12.	Ability to filter AD groups by root OU.

P.	Data Management System shall provide the following:
1.	Availability of fully automatic, scheduled backup of the database to any administrator defined location.
2.	Availability of a database restore utility that can be performed via web browser.

Q.	Software Registration Management shall provide the following:
1.	Software registration directly through dealer or the manufacturer.

R.	Photographic Badge Design shall provide the following:
1.	Functional integration with cardPresso photographic badge software via SQL database.
2.	Ability to link card to database data and include links to any of the customizable card holder fields, including date of birth, titles, initials, first or last name, and photograph.
3.	Ability to import Cardholder photographs or images from files.

S.	Contextual Help File shall provide the following:
1.	Annotation by hovering over fields.
2.	Documentation installation along with server software.

T.	Assa Abloy Aperio Integration:
1.	Software shall provide unified management of Aperio devices.
2.	Ability to communicate with up to 8 Aperio wireless locks per Aperio controller.
3.	Ability to store 100,000 users, bypasses Aperio 2,000 user limitation.
4.	Cabinet or door locks supported.
5.	Ability to share time schedules between regular door controllers an Aperio controllers.

U.	Software Navigation and Contextual Help:
1.	Offer contextual help file by hovering over fields, check boxes, drop-down menus.
2.	Ability to place objects into list format (such as panels, doors, user) for conducting comparisons between objects.
3.	Ability to edit attributes of objects from the list view.
4.	Software shall offer comprehensive documentation can be accessed through web interface, or accessed via start menu shortcut on host web server.

2.3	PRODUCT SUBSTITUTIONS
A.	        Substitutions: No substitutions permitted.

PART 3	EXECUTION

3.3	MANUFACTURER’S INSTRUCTIONS
Specifier Note: Article below is an addition to the CSI Section Format; please revise to suit project requirements and specifier’s practice.
A.	Compliance: Comply with manufacturer’s written data, including product technical bulletins, product catalog installation instructions and product carton installation instructions.

3.4	EXAMINATION
A.	Site Verification of Conditions:
1.	Verify that substrate conditions, which have either been previously installed under other sections, or that existing site conditions, are acceptable for product installation in accordance with manufacturer’s instructions.
2.	Verify that building doors, frames, walls, wire runs, related items and conditions are ready to receive work of this Section.

3.4	PROTECTION
A.	Other Trades: Protect installed work of other trades.

3.5	PREPARATION
A.	Project Planning Forms:
1.	Manufacturer Forms: Obtain and complete project planning forms from manufacturer of surveillance system; customize forms to be project specific.
2.	Final Setup: Review, adjust and prepare final documents to establish system software setup.

B.	  Record Setup Data:
1.	Record server and workstations setup data.
2.	Record controller address, features and access requirements for each location.
3.	Propose start and stop times for Time Zones, including holidays; match up for Door Schedule.
4.	Set up Access Privilege groups, Elevator Privilege groups, Auxiliary Relay Activation group, linking; list inputs and outputs for each Controller.

C.	Electrical Preparation:
1.	Ensure dedicated 120 VAC power circuits, conduit, raceways, back boxes, j-boxes, fittings, hardware and earth grounds supplied as necessary to provide complete working system.
2.	Ensure power supplies associated with electrified door hardware is installed.
3.	Ensure conduit for cable protection within walls, back boxes, door jambs, stubbed above drop ceilings, within closed ceilings, where exposed, and penetrating walls and ceilings, have been provided.
4.	Ensure back box installations in masonry have been completed.
5.	Ensure patching and painting items related to conduit, raceways, j-boxes, fittings hardware and earth grounds conduit and conduit installations has been done.
6.	Ensure cabling for alarm systems is installed and completed.

D.	Elevators:
Specifier Note: Installation of equipment and wiring to the elevator to be coordinated with the elevator contractor.
1.	Coordinate installation of wiring, card readers and relay’s to cab(s).
2.	Coordinate installation of wiring and equipment for elevator control, life safety to cab(s).
3.	Coordinate testing and commissioning of elevator system after installation of equipment.

E.	Information Services:
Specifier Note: Installation of equipment and wiring for information services to be coordinated with IT personnel.

1.	Ensure that dedicated phone lines and phone equipment have been provided and completed.
2.	Ensure that network drops are being installed and installation coordinated with the work of this section.
3.	Ensure coordination of Server and Client software installations with IT personnel.
4.	Ensure coordination of IT personnel prior to configuration and installation of Ethernet converters.

F.	Fire Alarm:
Specifier Note: Installation of equipment and wiring for the fire alarm panel to be coordinated with the fire contractor.

1.	Ensure coordination of installation, including wiring and equipment for the fire alarm panel to interface with access control alarm monitoring system, is undertaken.

3.6	INSTALLATION
A.	Shall comply with:
1.	IEEE 1100.
2.	NFPA 70.
3.	NFPA 72.
4.	NFPA 80.
5.	NFPA 101.
B.	Shall use the following methods:
1.	Install surface mounted units to finished substrates.
2.	Set units level, plumb and true to line and location.
3.	Comply with positioning requirements for disabled accessibility.
4.	Provide 120 VAC power circuits, conduit, raceways, back boxes, j-boxes, fittings, hardware and earth grounds as required to provide electrical requirements for access control systems.
C.	Cabling:
Specifier Note: Select the cabling system appropriate to the installation. Delete paragraphs that are not applicable.
1.	Raceway and Cable Tray: Install wiring in raceway and cable tray, except:
a.	Within consoles, cabinets, desks and counters.
b.	In accessible ceiling spaces.
c.	In gypsum board partitions where unenclosed wiring method may be used.
2.	Conduit: Install wiring in conduit, except:
a.	Within consoles, cabinets, desks and counters.
3.	J-Hooks: Install wiring in j-hooks and associated wire hardware.
4.	Conceal [Raceway and cable tray] [Conduit] [J-hooks and cables] except in unfinished spaces.
5.	Use NRTL-listed plenum cable in environmental airspaces, including plenum ceilings.
6.	Install cables without damaging conductors, shield or jacket.
7.	Use only Manufacturer recommended wiring, 
8.	Basic elevation drawings available from manufacturer upon request.  
9.	Advanced elevation, riser and point to point diagrams available from manufacturer for an additional fee, based on the complexity of the project, and the level of integration required with other systems.

D.	Grounding:
1.	Comply with IEEE 1100.
Specifier Note: To eliminate shock hazard and to minimize ground loops, common-mode returns, noise pick-up, cross-talk and other impairments, use the following.
2.	Ground cable shields, drain conductors and equipment.
3.	Bond shields and drain conductors to ground at only one point.

E.	System Software:
1.	Develop, install and test software and databases for complete and proper operation of systems involved.
2.	Register all Software within 30 days of onsite installation.

3.6	FIELD QUALITY CONTROL
Specifier Note: Use the following Articles only when manufacturer’s field services are desired to verify the quality of the installed components. Establish the number and duration of periodic site visits required by Manufacturer and specify below. Consult Manufacturer for services required. Delete if field services are not required.
A.	Written Reports: Have manufacturer of products supplied under this Section review Work involved in handling, installation/application, protection and cleaning of its product[s], and submit written reports in acceptable format to verify compliance of Work with Contract.
B.	Manufacturer’s Field Services: Provide manufacturer’s field services consisting of product user recommendations and periodic site visits for inspection of product installation in accordance with manufacturer’s instructions.
C.	Schedule site visits to review Work at stages listed:
1.	After delivery and storage of products, and when preparatory Work on which Work of this Section depends is complete, but before installation begins.
2.	Throughout progress of Work.
3.	[Twice] [______] during progress of Work at [25%] [______] and [60%] [______] complete.
4.	Upon completion of Work, after cleaning is carried out.
D.	Obtain reports within [Five] [______] days of review and submit.

3.7	TESTING & VERIFICATION
Specifier Note: Provide test descriptions in sufficient detail to fully describe the specific tests to be conducted to demonstrate conformance with the specification.
A.	Perform tests recommended and required by manufacturer to verify required performance of all products manufactured and /or supplied by Vicon Industries.
1.	Complete system diagnostics and operation verification.
2.	Prepare specific plan for system testing, start-up and demonstration.
3.	Develop acceptance test concept and specifics.
4.	Test each circuit and component of each system. System components with battery back-up to operate on battery power for not less than [10] percent of calculated battery operating time. Provide special equipment and software if testing requires special or dedicated equipment.
5.	Operational Test: Demonstrate product capability and compliance with requirements.
6.	Remove and replace malfunctioning devices and circuits and retest.
7.	Complete installation and start-up checks in accordance with manufacturer’s written instructions.
8.	Maintain strict security during installation of equipment and software. Secure rooms housing the Server software and workstations.

3.8	DEMONSTRATION
Specifier Note: A training program is required to educate personnel with the required level of system familiarity to provide a common working knowledge concerning all aspects of the system.
A.	Training Program:
1.	Provide training to Owner’s personnel to adjust, operate and maintain access system.
2.	Two weeks prior to the start of the program, submit proposed dates for training.
3.	Develop separate training modules consisting of at least, but not limited to 1 hour per group, based on the level of knowledge required by the specific group.
4.	Provide group specific operator manuals covering all areas of hardware/software required.
5.	Groups:
a.	Computer system administration personnel tasked with managing and maintaining databases and updating and maintaining software.
b.	Operators tasked with preparing and imputing credentials to staff/users.
c.	Operators tasked with configuring hardware and or software features and functions.
d.	Security personnel.

.
3.9	COMPLETION & CLEANUP
A		Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION