IP VIDEO SURVEILLANCE SYSTEM
	SECURITY SYSTEM
28 23 00 VIDEO SURVEILLANCE
PART 2 - PRODUCTS

2.01	GENERAL

A.	All equipment and materials used shall be standard components, regularly manufactured, 
regularly utilized in the manufacturer’s system.

B.	All systems and components shall have been thoroughly tested and proven in actual use.

C.	All systems and components shall be provided with the availability of a toll free 24-hour 
immediate technical assistance for either the dealer/installer at no charge.

D.	All systems and components shall be provided with an explicit manufacturer warranty.

E.	All Cameras, NVRs, DVRs, and Workstations shall be available to be shipped pre-configured and programmed to the systems requirements by the manufacturer.

2.02	DIGITAL VIDEO RECORDING MANAGEMENT AND NETWORK SOFTWARE – GENERAL 

A.	The Video Management Software (VMS) shall be a browser-based application that shall meet the requirements of business and government surveillance applications. It shall provide the web client with a single point of management for the entire system functions and not require a thick client. The Recording Servers, Application Servers, Web Servers, as well as IP cameras and encoders (edge devices) shall be added, configured and operated using the configuration section of the application. The Recording Servers, Application Servers, Web Servers, as well as IP cameras and encoders (edge devices) shall be added, configured and operated using the configuration section of the application. The VMS shall provide a complete and comprehensive application for the operation and maintenance of a video surveillance system. It shall provide full live digital video and audio surveillance over a standard 1 Gbps network.

B.	The VMS shall support recording, playback and archiving of video in standard industry compression formats, including H.265, H.264 and M-JPEG.

C.	The application shall be based on true open standards (ONVIF Profile G) and shall be a thin client architecture and shall be centrally licensed. The application software shall be COTS compatible or shall also be available preloaded on a manufacturer certified application/web server or recording server (NVR). A Redundant Application server shall be able to be configured to take over in the event of Application Server failure. A failover NVR shall be able to be configured to take over in the event of an NVR failure.

D.	There shall be three license tiers that are associated with both a number of edge devices and a specific feature set. Licensing shall be based on a per edge device basis.

E.	The software shall run on a COTS PCs with a minimum of Intel Core i7 processor, 16 GB of RAM and 5 GB of disk space for installation and a minimum of 75 GB of disk space for a recording device. The software shall run on the Microsoft® Windows® 10 64-bit; Windows 2008, 2012 or 2016 64-bit Server operating systems. The Client (web) shall also be able to run on Windows 7 O.S.

F.	The VMS shall offer easy to use tabs to access configuration and a dashboard that monitors the 
	systems health. The monitoring screen shall show the video display area with a list of available 
	resources. Multiple display views shall be configurable and a variety of display layouts shall be 
	available. Multiple monitors shall also be supported.

G.	Live video shall stream through the Recording Server (NVR) with auto fail over to the camera. PTZ shall be available from the live video and presets and tours shall be configurable. Digital zoom shall be provided on all video displays. 

H.	A web-based interface shall be provided to access the VMS from any enabled device. It shall work with Internet Explorer 11 and Firefox. Chrome shall be able to be used with the Valerus Chrome extension from the Chrome store. It shall provide live viewing, playback and PTZ controls. A Mobile App shall be available for both Apple and Android smart phones and tablets. The mobile application shall be able to view live or recorded video. It shall be able to view concurrent multiple video stream, up to 4 on phones and 9 on tablets. The mobile application shall have full control of PTZ, including presets, and quick and simple playback. Pinch to zoom on live and recorded video shall be available.

I.	The application shall provide an easy to use icon from the display page for Export to save a video clip. This clip shall be able to be archived in MP4 format and shall be authenticated in the player according to the ONVIF spec. 

J.	The application shall support playback from the main screen without leaving the live video viewing area. Clicking a Playback from time icon shall allow selecting the playback to start from a specific date and time using standard calendar tools.

K.	The software shall be provided on the manufacturer’s website for easy download.

L.	Events shall be setup in the configuration area. Pre-event recording shall be supported and there shall be event notification.

M.	The VMS shall support integration with Vicon’s VAX Access Control System and shall be accessed using a simple click of a tab. The Access Control interface shall open in a popup window that can be used in conjunction with the VMS. 

N.	Enhanced edge-based analytics shall show bounding boxes around detected objects in live and playback video.

O.	Authorization roles shall be configurable; these roles shall then be listed in the Resources list on the monitoring display screen. This Resources list can be viewed in a hierarchy view with these groups or as a flat list. 

P.	Video Masking shall be available centrally through the VMS. This shall allow users with the correct authority to unmask video as needed using an icon on the display screen. There shall be an unmask feature on live and playback video.

Q.	A Quick Configuration wizard shall be provided for a streamlined process for typical and basic system setup with minimal input required.

R.	Four search functions shall be available, museum search (on those cameras equipped with this ability), thumbnail search, events framework search for use with third party integration (an add-on) and analytics search (separate license required).

S.	Capability for 360° lens dewarp shall be available for use with cameras with fisheye lenses. Dewarping shall happen within the VMS.

T.	The VMS shall offer integration with Active Directory (AD) to allow all user management from a central IT manager’s station.

U.	There shall be an override mode when using AD to allow operating in case AD communication is lost.

V.	Multi-language support shall be available. All text in the user interface shall be translated to the selected language. 

W.	A Backup and Restore for system settings shall be available.

X.	Keypads and PLC controls shall be supported. Numeric IDs for devices shall be configurable for use with these controls. These devices shall be able to control remote monitors.

Y.	A Central Software Upgrade interface shall provide the ability to upgrade the entire system by pushing the upgrade from the Application Server out to all devices on the system.

Z.	The system shall support IPv4/IPv6 and HTTPS.

AA.	A Gateway module shall be available to bridge migration from a legacy ViconNet Video Management System to this VMS and use the old system resources.

BB.	The system shall have built in Log Collection from all system PCs, making it easier to troubleshoot problems. An advanced tool shall be provided. An 

CC.	The system shall accept external text strings from third party systems.

DD.	Alarm notification shall be both visual and audible.

EE.	A Report button shall generate an Excel report of the devices sorted by their hosting NVRs or a flat list.

FF.	Devices shall be able to be replaced or moved, for load balancing purposes.

GG.	An NVR Failover unit shall be able to be configured to take over in the event of an NVR failure.

HH.	The VMS shall support integration with a pre-defined Video Analytics (separate license required).

II.	A Mapping function shall be provided that allows the placement of resource devices on any imported map. The map shall be either a static or live map.

JJ.	An Event Database shall exist to store any event that occurs in the system. From the Event Search screen, a query shall be able to be created to search for any event that occurs on the system from any resource in the system.

KK.	A video clip, either in live or playback, shall be able to be bookmarked for easy referral.

LL.	The ability to use mobile devices as mobile cameras shall be available. The mobile device shall be able to receive event alerts.

MM.	The VMS shall be able to accept partner systems through an integration framework.

NN.	      A Snapshot function shall be provided to capture video from live or playback; this 
      snapshot shall be able to be saved.

OO.	An Audit Log shall be available to track every user’s actions.

PP.	      Keypads/PLC shall have the ability to call up other remoted monitors. 

A thick-client solution shall be available for users who don’t want to use a browser

2.03	VIDEO MANAGEMENT SOFTWARE – SETUP, CONFIGURATION AND SECURITY

A.	The software shall offer a full multi-user authorization login application. This application shall offer levels of authorization based on functions. In addition, a full setup utility shall be available for the Administrator to configure additional users as well as authorization roles. User authorization shall be configurable for specific system operations. Authorization permission setup shall be performed using the Authorization Roles screen; rights shall be available to configure from the Authorization Roles screen. Permissions shall provide authority to perform all system functions. The software shall offer a full multi-user authorization process as follows:
1.	Authorization Roles shall be created once globally. Users and groups on an AD server shall be able to be imported and become a group in the VMS.
2.	Users shall be created once globally and shall be given rights to particular roles.
3.	Authorization Roles shall be authorized and given specific permissions.
4.	There shall be no virtual limit on the number of groups and users that can be authorized in the software.
5.	The software shall allow for each group to be authorized or denied access to:
a.	Search.
b.	Configuration and User Management.
c.	Dashboard.
d.	Video and audio (media) export.
e.	Override masking.
f.	User settings.

B.	All users created shall be able to log in to the system. A user, given appropriate access, shall be able to remotely configure components connected to the network. 

C.	The software shall permit viewing of live video from any edge device connected to any recording server on the network.

D.	An Export icon shall be provided that simplifies the process of exporting video and creating archives and saving video to media, such as: USBs, CD, DVDs or solid-state drives. An embedded player shall be optional with each exported/archived video clip for playback on any machine if configured to do so. 

E.	The software shall provide an easy-to-program menu selection for creating rules that shall determine system reaction (trigger) when an event occurs. An event shall be selectable and then the trigger for the rule shall be configured. 

F.	Multiple devices shall be able to be associated with an event. When the event occurs, it shall trigger the rule. Actions shall be configurable as On and Off. Actions for an event shall be display live video, display a view, go to a preset, operate a relay, run a PTZ tour, run a view tour, start a URL or delay.

G.	The software shall provide a method for scheduled recording of cameras/encoders and microphones. These schedules shall be able to be based on rules that shall be configurable for the actions the system shall take upon an event. These schedules shall be accessible on the recording tab in device configuration.

H.	Scheduling shall allow an authorized user to create and schedule recording that shall include but not be limited to: 
1.	Creating how often schedules should repeat, weekly, monthly, yearly or never. This shall determine the schedules priority level. If schedule times overlap, system shall prioritize schedules.
2.	Schedules shall be available when configuring recording and rules, which shall save the need to create multiple schedules.
3.	Sequencing cameras, including multi-screen displays.
4.	Record cameras at different qualities and frame rates from any recorder on the network.
5.	The Schedule shall allow the running of preconfigured combinations of camera, sensor and PTZ programmed routines.

I.	The system shall consist of:
1.	An Application/Web Server shall act as the main system server. It shall be a Windows service. All global configuration of the system shall be stored on this server.
2.	Recording Servers (NVRs) shall be a Windows service that provides communication, streaming and recording of live and playback video and audio from cameras and encoders.
3.	Redundant Application Server (optional) that can take over as primary Application Server in case of a failure of the primary Application Server.
4.	Client Viewer and Administration: All Viewing and Administration stations shall be browser-based and offer access to all recording and live streams.
5.	Mobile Client, for IOs and Android smartphones and tablets, support securely connecting to the VMS using HTTPS to view live and recorded video from any device on the system.

J.	Device configuration shall have the ability to be configured for system recognition and operation. Valid devices shall be:
1.	Cameras, fixed or with integrated PTZ
2.	Microphones
3.	Encoders
4.	Sensors
5.	Relays

N.	Authentication: The video from the cameras shall be able to verify the authentication of the video and present an authentication symbol on the displayed video for recorded playback through the player when enabled only on export.

2.04	VIDEO MANAGEMENT SOFTWARE – USER INTERFACE

2.04.1	The software shall provide a user interface that shall allow monitoring of live and playback video 
	and configuration of the system using easy to use tabs. The application shall display a Login 
	Window that shall consist of a User Name and Password field. A default user name and 
	password shall be available upon first login. These shall be configurable for increased security; 
	there shall be an option to enforce a complex password.

The user interface shall serve operators, supervisors and system administrators. The monitoring display area shall allow the operator to select the number of tiles to display. 

B.	The Monitoring screen shall provide the following:
1.	The Resources list of all devices in the system.
2.	The Resources list shall be able to be viewed as a flat list of devices or a hierarchy list based on user configured groups. The Resources shall include the names of the device and an icon depicting the type of device:
a.	Video Channels (cameras) connected, differentiating between PTZ and fixed cameras.
b.	Audio Channels (microphones).
c.	Views
d.	Tours
e.	Web Pages
f.	Relay Outputs
3.	A display area that offers a wide variety of display configurations up to 36 tiles. Viewing full screen shall also be available.
4.	More views shall be easily added by clicking the plus sign to create new view tabs while not losing the default view.
5.	Controls for the display area to change the layout, stop all displays, export and synchronize playback shall be available and control current selected tab.
4.	Camera controls for playback, PTZ control, digital zoom, unmask, export and configuration settings shall display at the top of a tile when the mouse hovers. These shall be able to be locked in place.
5.	Playback controls for looping a video section, slow mode, play from time, rewind, fast rewind, pause, forward, fast forward, back to live video and go to current time shall be visible when cameras go to playback. 
5.	Access to all available programming menus.
6.	Viewing of live devices shall be performed by dragging a device to any tile. Audio devices shall not take up an entire tile but shall display in a smaller area below the video tiles

C.	Access to Configuration menus and the Dashboard shall be available by clicking a tab at the top of the screen. A Home page shall present upon first time in the Configuration screen, with easy to use icons and links to the configuration options.

2.05	VIDEO MANAGEMENT SOFTWARE – VIDEO QUALITY

A.	The VMS shall support any resolution video, jpeg and H.264/H.265 compression.

2.06	VIDEO MANAGEMENT SOFTWARE – ADD-INS 

A.	An Access Control system shall be available for integration. This system shall meet the requirements of business and government access control systems. The system shall monitor and control facility access as well as video detection, temperature and communications loss monitoring. The system shall provide control and access to users on Local Area Networks (LAN), Wide Area Networks (WAN), wireless networks and the Internet. The system shall provide video viewing playback and PTZ control from the VMS.

B.	A Video Analytics program shall be available for integration. This system shall allow real-time detection, business intelligence and search capabilities.

C.	A method to add partner systems shall be provided through an integration framework. It shall support the Thermal Radar sensor. 

2.07	VIRTUAL MATRIX DISPLAY CONTROLLER OPTION

A.	A Virtual Matrix Display Controller (VMDC) shall be available for digital video recording management and network software. The VMDC shall provide the following capabilities:
1.	Display any analog or IP camera on the network on any monitor on the network.
2.	Allow the use of both 4 x 3 and 16 x 9 monitors.
3.	Allow control of the system from VMDC PC GUI, PLC or a supported keypad.
4.	Supports 4 keypads and up to 6 monitors per workstation.
5.	Map capability.

B.	A keypad shall be provided to provide the following functions:
1.	Control PTZ functions.
2.	Control camera switching to monitor.

The VMDC shall be available as software ready to be installed on a suitable PC, preinstalled on a rack or tower unit. 

2.08	ENCODER OPTIONS

A.	Encoders shall be available that convert both high-definition analog or standard analog camera inputs into streamed IP video data:
1.	A 16-channel unit shall be available.

2.09	APPROVED MANUFACTURERS

A.	The Video Management System shall be Vicon’s Valerus. This software shall be available on Vicon’s website. The software shall be available preinstalled on manufacturer certified hardware.

B.	The encoders shall be Vicon model VLR-ENC-16 (16-channel). This shall have a separate specification.

2.10	DIGITAL SERVERS 

A.	The digital application server and recording server (NVR) shall be a PC computer with a Microsoft® Windows® 10 LTSB* (64-bit) operating system. It shall be fully equipped with the Digital Video Management Software. It shall require an external monitor, keyboard and mouse for operation. A mini recording server shall also be available.

B.	As a minimum, the server shall have Intel® Core™ i7 processor and a minimum of 16 GB RAM; the mini version shall have an Intel® Core™ i5 processor and a minimum of 4 GB of RAM memory. The units shall have USB ports and monitor outputs. 

C.	The server shall be housed in a desktop or rack-mount case with all suitable connectors available on the back panel**. It shall be constructed of steel and plastic materials. It shall also be operated indoors in a temperature range not to exceed 32 to 104° F (0 to 40° C) and a humidity range not to exceed 0 to 95% relative, in a non-condensing atmosphere. The server shall employ a Universal Voltage Power Supply requiring 105 - 240 VAC @ 50 - 60 Hz. A rack-mounting bracket kit shall be provided.

*A full windows O.S. is available on request. **The desktop and 1U rack-mount versions support up to a certain drive size. Larger drive capacity is available, but may require a larger tower or 2U chassis. Contact your sales representative.

D.	The recording server shall offer internal hard-drive storage with the following capacities:
1.	1 TB.
2.	2 TB.
3.	3 TB.
4.	4 TB.
5.	6 TB.
6.	8 TB
7.	10 TB
8.	12 TB
9.	14 TB
10.	16 TB
11.	20 TB

E.	The application server can be a standalone unit with no storage capability or an all-in-one unit included in the recording server.

F.	The mini recording server shall offer internal hard-drive storage with the following capacities:
1.	1 TB.
2.	2 TB.
3.	4 TB.
4.	6 TB.
5.	8 TB

G.	A client viewing station shall be available with 2 or 4 monitor outputs.

H.	A model shall be available with internal RAID storage, 4-bay, 8-bay, 12-bay and 24-bay models. These shall be available in the following capacities (RAID 5; available in RAID 6 with slightly lower storage capacities): 
1.	8.5 TB (1U, 4-bay)
2.	11 TB (1U, 4-bay)
3.	17 TB (1U, 4-bay).
4.	22 TB (1U, 4-bay).
5.	34 TB (1U, 4-bay).
6.	53 TB (2U, 8-bay).
7.	62 TB (2U, 12-bay).
8.	83 TB (2U, 12-bay).
9.	104 TB (2U, 12-bay).
10.	125 TB (2U, 12-bay).
11.	174 TB (4U, 24-bay).
12.	218 TB (4U, 24-bay).
13.	262 TB (4U, 24-bay).

I.	The servers shall be preloaded with Valerus Video Management Software.     
2.11	
ELECTRICAL SPECIFICATIONS 

A.		Input Voltage:	105-240 ±10% VAC, 50/60 Hz.	
B.		Current:	0.66 A @ 115 VAC; 0.33 A @ 230 VAC.
Mini: 0.33A @ 115 VAC; 0.16A @ 240 VAC.
4-bay internal storage: 5 A @ 115VAC; 3 A @ 230 VAC
8-bay internal storage: 9.5 A @ 115VAC; 4.5 A @ 230 VAC.
12-bay internal storage: 10 A @ 115VAC; 8 A @ 230 VAC
24-bay internal storage: 10 A @ 115VAC; 8 A @ 230 VAC.	
C.		Power Consumption:  	
76 W. Mini: 38 W.
4-bay internal storage:300 W nominal, includes redundant power supply
8-bay internal storage: 650 W nominal, includes redundant power supply and redundant OS. 
12-bay: 875 W nominal, includes redundant power supply and redundant OS.
24-bay internal storage: 975 W; includes redundant power supply and redundant OS.	
D.		CPU	Intel® Core™ i7. Mini: Intel i5.	
E.		RAM Memory	16 GB minimum; mini: 4 GB.	
F.		Heat Output:  	266 btu/hour. Mini: 133 btu/hour.	
G.		Storage:	1 TB to 20 TB. Depending on model.	
H.		Operating System:	Microsoft Windows 10 LTSB, 64 bit.	
I.		LAN Interface:	100/1000 Base T Ethernet interface on main board.	
J.		Front Panel
Controls/Indicators:	
Power, network activity LEDs, USBs.	
K.		Certifications:	FCC Class A.	

2.12	MECHANICAL SPECIFICATIONS 

A.		Application:	Indoor.	
B.		Mounting:	Desktop, mini desktop, tower or rack unit mounted in a standard EIA compliant rack, 19 in. (483 mm) wide opening. Rack height is 1.75 in. 
(44 mm) or 1 RU.	
C.		Dimensions-Rack:  	Width (W): 19.0 in. (483 mm).
Depth (D): 16 in. (406 mm).
Height (H): 1.75 in. (44.45 mm), 1 RU.
4-bay internal storage: Width (W): 19 in. (483 mm).
         Depth (D): 22 in. (660 mm).
         Height (H): 1.75 in. (89 mm).
8/12-bay internal storage: Width (W): 19 in. (483 mm).
         Depth (D): 26 in. (660 mm).
         Height (H): 3.5 in. (89 mm).
24-bay internal storage: Width (W): 19 in. (483 mm).
         Depth (D): 27.5 in. (711 mm).
         Height (H): 6.9 in. (176 mm).	
D.		Dimensions-Desktop	Desktop: Width (W): 3.75 in. (95.25 mm).
        Depth (D): 10.5 in. (266.7 mm).
        Height (H): 9.5 in. (241.3 mm).
Mini: Width (W): 7.9 in. (200 mm).
         Depth (D): 7.75 in. (197 mm).
         Height (H): 3.5 in. (89 mm).	
E.		Weight-Rack:	18.2 lb. (8.3 kg) approximately.
4-bay internal storage: 28.7 lb (13 kg).
8-bay internal storage: 46.3 lb (21 kg).
12-bay storage:
24-bay internal storage: 82.0 lb (37 kg).	
F.		Weight- Desktop:	Desktop: 8.1 lb. (3.7 kg) approximately. Mini: 2.5 lb (1.1 kg)	
G.		Construction:	Steel and plastic.	
H.		Color:	Black.	

2.13	ENVIRONMENTAL SPECIFICATIONS 

A.	Operating 
Temperature Range:	
32 to 104ºF (0 to 40ºC).	
B.	Operating 
Humidity Range:	
0 to 95%, non-condensing.	

2.14	CERTIFICATIONS

A.	FCC, Class A

2.15	WARRANTY

A.	3 years, parts and labor 

2.16	APPROVED MANUFACTURERS

C.	The Video Management System shall be Vicon’s Valerus. The Application Server shall be models VLR-APPSRV-A (desk-top) and VLR-APPSRV-A-RK (rack-mount). The Recording Server shall be models VLR-XTB-A (preloaded desk-top) and VLR-XTB-A-RK (preloaded rack-mount). The models with internal RAID shall be VLR-TB-R5-A. The mini server shall be model VLR-MINI-XTBV1. (X is the hard drive size). The Viewing Station shall be VLR-CLIENT-A/VLR-CLIENT-4-A (desk-top; 2 or 4 monitor) and VLR-CLIENT-A-RK/VLR-CLIENT-4-A-RK (rack-mount; 2 or 4 monitor).

2.17	OUTDOOR FIXED DOME VANDALPROOF DAY/NIGHT IP CAMERA 

A.	The outdoor fixed dome camera shall incorporate a camera/lens combination. The dome camera shall be available for indoor/outdoor surface mounting. The high-resolution day/night camera shall have true WDR and IR capability and include an integral varifocal autoiris lens. The lens shall be motorized to allow for remote configuration of zoom and focus (motorized focus and zoom). Day/night operation shall be achieved using a built-in IR-cut filter. IR distance shall be 98 ft (30 m) with smart IR LED technology. A clear polycarbonate lower dome that is secured by tamperproof screws shall be included. 
B.	The camera position shall have a three-direction adjustment, allowing for adjustment of pan, tilt and lens rotation (roll), for any angle of view required.
C.	The dome camera shall have smart encoding, which monitors the amount of motion in a scene, resulting in overall savings in storage and bandwidth without sacrificing video quality.
D.	The dome camera shall be powered by PoE, 24 VAC or 12 VDC. 
E.	The dome camera shall have triple streaming video and support H.264/H.265, and 
M-JPEG (3rd stream only) compression. The camera shall be available in 1080p
(2 megapixel), 4 MP and 5 MP resolution. There shall be additional 2 MP models available with ultra-high-sensitivity and extended WDR (132 dB).
F.	Camera features shall include electronic iris, AGC, WDR, white balance, corridor, mirror, privacy masks, ROI (Region of Interest), museum search and motion detection.
G.	The dome camera shall meet the FCC requirements for a Class A device. It shall include support for the industry-standard ONVIF interface. It shall be IP66-rated to withstand rain, dust and vandalism and IK10 rated for impact resistance.
H.	The dome camera shall provide a slot for an SD card for local storage.
I.	There shall be mounting accessories to allow pendant mounting, mounting to a 4x4 electrical box and a back box for ease of cabling.
J.	The fixed-position camera dome shall meet or exceed the following design and performance specifications.
2.18	FIXED DOME CAMERA AND OPTICS SPECIFICATIONS

A.	Imaging Device:			2/4 MP: 1/3-inch progressive scan CMOS; 
				2 MP-XW: 1/2.8-inch progressive scan CMOS; 
				2 MP-XS: 1/1.9-inch progressive scan CMOS; 
				5 MP: 1/1.8-inch progressive scan CMOS;
B.	Max. Resolution:		1080p (2 MP), 4 MP and 5 MP models
C.	Shutter Speed:			2 MP/4 MP: 1 - 1/32,000 sec
				2 MP-XW/2 MP-XS/5 MP: 1 - 1/30,000 sec
D.	Automatic Gain Control:		On/Off selectable
E.	Sensitivity:			2 MP/2 MP-X/4 MP: Color: 0.01 lux; B&W: 0 lux (IR On)
                                                    @f/1.4, 30 IRE, AGC On
MP-XS: Color: 0.002 lux; B&W: 0.0006 lux/0 lux (IR On) @f/1.5, AGC On
5 MP: Color: 0.1 lux; B&W: 0.02 lux/0 lux (IR On) @f/1.5, AGC On
F.	Wide Dynamic Range		True WDR, 120dB; XW: 132dB
G.	Tilt and Horizontal
Adjustment			3-axis adjustment: pan (360°), tilt (80°) and roll (lens may be rotated on 
				its axis 360°)
H.	Lens Adjustment:		Motorized focus and zoom adjustment 
I.	Focal Length:			2 MP/4 MP: 2.7-12 mm varifocal 
				2 MP-XW: 3-10.5 mm varifocal
				2 MP-XS/5 MP: 3.6-10 mm varifocal
J.	Horizontal Field of View:		2 MP: 85°- 29.8°
				2 MP-XW: 92.5°- 33°
				2 MP-XS: 101.8°- 44.3°
				4 MP: 94°- 31°
				5 MP: 87.9°- 38.4°
K.	IR Distance:			98 ft (30 m) 

2.19	ELECTRICAL SPECIFICATIONS

A.		Input Voltage:	12 VDC, 24 VAC or PoE.	
B.		Current (IR On):	12 VDC: 750 mA;
24 VAC: 375 mA..	
C.		Power Consumption (IR On):	<9 W.	
D.		Connectors:	Power: standard jack for adapter. 
Network/PoE: RJ-45. 
Alarm: screw terminal. 
Audio: RCA jack. 
Slot for SD card. 
 Composite output provided for installation.	
E.	Radio Frequency	             FCC Class A; CE
 Emission Rating:
2.20	NETWORK VIDEO TRANSMISSION SPECIFICATIONS

A.		Compression:	H.264/H.265, M-JPEG.	
B.		Users:	Up to 10 clients.	
C.		Video Resolution:	1080p (2 MP) Major streams: 1920x1080, 1280x720/960
4 MP Major streams: 2592x1520, 2048x1520, 
2304x1296,1920x1080, 1280x720/960
5 MP: Major streams: 2592x1944, 2592x1520, 
2048x1520, 2304x1296,1920x1080, 1280x720/960.	
D.		Frame Rate:	Max 30 fps at 1920x1080 (1080p).	
E.		Network Interface:	10Base-T, 100Base-TX.	
F.		Streams: 	Triple streaming.	
G.		Web Browser:	Internet Explorer.	
H.		Image Settings	Day/night mode; corridor and mirror; configurable 
brightness, contrast, hue, sharpness, saturation; white 
balance, AGC; Electronic Shutter, automatic or manual;
true WDR (120dB or 132dB on XW model); privacy 
masks (4); motion detection (4); ROI (8); DNR	
I.		Video Content Analytics:	EIS, Defog, Video Contents Analysis (Intrusion 
Detection, Line Cross Detection, Museum Search and Camera Tampering – Scene Change, Defocus, 
Low/High Brightness)	
J.		Supported Protocols:	IPv4/IPv6, TCP, HTTP, HTTPS, RTSP, RTCP, RTP, 
SMTP, DHCP, NTP, FTP DDNS, UDP, uPnP,QoS, 
ARP, IGMP, SNMP (V3), TLS, SSL, 802.1x, PPPoE, 
DNS, ICMP	

2.21	OPERATIONAL

A.		Alarm Capabilities:	2 inputs, 1 output. 	
B.		Audio Streaming:	1 input, 1 output; 2-way G.711	
C.		Control Display:	Web browser menu-driven system allowing full configuration of the camera	
D.		Tilt and Horizontal Adjustment:	
3 axis adjustment, pan, 360°; tilt, 80° and rotation about its axis (360°; roll/azimuth).	
E.		Lens Adjustment:	Motorized zoom and focus.	

2.22	ENVIRONMENTAL SPECIFICATIONS

A.		Operating Temperature:	
-40 to 140° F (-40 to 60°C).	
B.		Humidity:	Up to 90% relative, non-condensing	
 
2.23	MECHANICAL SPECIFICATIONS

A.		Construction:	Aluminum housing with clear polycarbonate plastic dome. Tamperproof screws.	
B.		Dimensions:	Height: 4.76 in. (121 mm).  
Diameter: 5.91” (150 mm).	
C.		Weight:	2.09 lb (0.95 kg)	
D.		Camera Mount:	Indoor or outdoor. Surface mount (with optional mounting kit), pendant on standard 1 ½” NPT (with optional pendant adapter). May be mounted to a 4x4 electrical box with an adapter plate.	

2.24	CERTIFICATIONS

A.	CE
B.	UL 
C.	FCC, Class A
D.	IP66
E.	IK10

2.25	WARRANTY

A.	3 years, parts and labor 

2.26	APPROVED MANUFACTURERS

A.	The outdoor fixed color IP dome camera shall be Vicon Industries Model V942D-W312MIR, V942D-W312MIR-XW, V942D-W312MIR-XS, V944D-W312MIR, and V945D-W310MIR.
B.	The fixed dome, day/night camera shall be available to be shipped pre-configured and programmed to the systems requirements by the manufacturer.

2.37	OUTDOOR IP BULLET CAMERA 

A.	The outdoor fixed bullet camera shall incorporate a camera/lens combination. The camera shall be available for indoor/outdoor surface mounting. The high-resolution day/night camera shall have true WDR and IR capability and include an integral varifocal autoiris lens. The lens shall be motorized to allow for remote configuration of zoom and focus (motorized focus and zoom). Day/night operation shall be achieved using a built-in IR-cut filter. IR distance shall be 98 ft (30 m) with smart IR LED technology. A clear polycarbonate lower dome that is secured by tamperproof screws shall be included. 
B.	The camera position shall be adjustable, using the integral mount. A sunshield shall be provided.
C.	The camera shall have smart encoding, which monitors the amount of motion in a scene, resulting in overall savings in storage and bandwidth without sacrificing video quality.
D.	The camera shall be powered by PoE, 24 VAC or 12 VDC. 
E.	The camera shall have triple streaming video and support H.264/H.265, and M-JPEG (3rd stream only) compression. The camera shall be available in 1080p (2 megapixel), 4 MP and 5 MP resolution. There shall be additional 2 MP models available with ultra-high-sensitivity and extended WDR (132 dB).
F.	Camera features shall include electronic iris, AGC, WDR, white balance, corridor, mirror, privacy masks, ROI (Region of Interest), museum search and motion detection.
G.	The camera shall meet the FCC requirements for a Class A device. It shall include support for the industry-standard ONVIF interface. It shall be IP66-rated to withstand rain, dust and vandalism and IK10 rated for impact resistance.
H.	The camera shall provide a slot for an SD card for local storage.
I.	There shall be a back box for ease of cabling.
J.	The camera shall meet or exceed the following design and performance specifications.

2.27	BULLET CAMERA AND OPTICS SPECIFICATIONS

A.	Imaging Device:		2/4 MP: 1/3-inch progressive scan CMOS; 
				2 MP-XW: 1/2.8-inch progressive scan CMOS; 
				2 MP-XS: 1/1.9-inch progressive scan CMOS; 
				5 MP: 1/1.8-inch progressive scan CMOS;
B.	Max. Resolution:	1080p (2 MP), 4 MP and 5 MP models
C.	Shutter Speed:		2 MP/4 MP: 1 - 1/32,000 sec
				2 MP-XW/2 MP-XS/5 MP: 1 - 1/30,000 sec
D.	Automatic Gain Control:	On/Off selectable
E.	Sensitivity:		2 MP/2 MP-X/4 MP: Color: 0.01 lux; B&W: 0 lux (IR On)
                                                    @f/1.4, 30 IRE, AGC On
MP-XS: Color: 0.002 lux; B&W: 0.0006 lux/0 lux (IR On) @f/1.5, AGC On
5 MP: Color: 0.1 lux; B&W: 0.02 lux/0 lux (IR On) @f/1.5, AGC On
F.	Wide Dynamic Range	True WDR, 120dB; XW: 132dB
G.	Tilt and Horizontal
             Adjustment		3-axis adjustment: pan (360°), tilt (80°) and roll (lens may be rotated on 
				its axis 360°)
H.	Lens Adjustment:	Motorized focus and zoom adjustment 
I.	Focal Length:		2 MP/4 MP: 2.7-12 mm varifocal 
				2 MP-XW: 3-10.5 mm varifocal
				2 MP-XS/5 MP: 3.6-10 mm varifocal
J.	Horizontal Field of View:		2 MP: 85°- 29.8°
				2 MP-XW: 92.5°- 33°
				2 MP-XS: 101.8°- 44.3°
				4 MP: 94°- 31°
				5 MP: 87.9°- 38.4°
K.	IR Distance:		98 ft (30 m) 

2.28	ELECTRICAL SPECIFICATIONS

A.		Input Voltage:	12 VDC, 24 VAC or PoE.	
B.		Current (IR On):	12 VDC: 833 mA;
24 VAC: 427 mA..	
C.		Power Consumption (IR On):	<10 W.	
D.		Connectors:	Power: standard jack for adapter. 
Network/PoE: RJ-45. 
Alarm: screw terminal. 
Audio: RCA jack. 
Slot for SD card. 
 BNC Composite output provided for installation.	
E.	Radio Frequency	             FCC Class A; CE
 Emission Rating:

2.29	NETWORK VIDEO TRANSMISSION SPECIFICATIONS

A.		Compression:	H.264/H.265, M-JPEG.	
B.		Users:	Up to 10 clients.	
C.		Video Resolution:	1080p (2 MP) Major streams: 1920x1080, 1280x720/960
4 MP Major streams: 2592x1520, 2048x1520, 
2304x1296,1920x1080, 1280x720/960
5 MP: Major streams: 2592x1944, 2592x1520, 
2048x1520, 2304x1296,1920x1080, 1280x720/960.	
D.		Frame Rate:	Max 30 fps at 1920x1080 (1080p).	
E.		Network Interface:	10Base-T, 100Base-TX.	
F.		Streams: 	Triple streaming.	
G.		Web Browser:	Internet Explorer.	
H.		Image Settings	Day/night mode; corridor and mirror; configurable 
brightness, contrast, hue, sharpness, saturation; white 
balance, AGC; Electronic Shutter, automatic or manual;
true WDR (120dB or 132dB on XW model); privacy 
masks (4); motion detection (4); ROI (8); DNR	
I.		Video Content Analytics:	EIS, Defog, Video Contents Analysis (Intrusion 
Detection, Line Cross Detection, Museum Search and Camera Tampering – Scene Change, Defocus, 
Low/High Brightness)	
J.		Supported Protocols:	IPv4/IPv6, TCP, HTTP, HTTPS, RTSP, RTCP, RTP, 
SMTP, DHCP, NTP, FTP DDNS, UDP, uPnP,QoS, 
ARP, IGMP, SNMP (V3), TLS, SSL, 802.1x, PPPoE, 
DNS, ICMP	

2.30	OPERATIONAL

A.		Alarm Capabilities:	2 inputs, 1 output. 	
B.		Audio Streaming:	1 input, 1 output; 2-way G.711	
C.		Control Display:	Web browser menu-driven system allowing full configuration of the camera	
D.		Tilt and Horizontal Adjustment:	
Integral wall mount adjustment.	
E.		Lens Adjustment:	Motorized zoom and focus.	

2.31	ENVIRONMENTAL SPECIFICATIONS

A.		Operating Temperature:	
-40 to 140° F (-40 to 60°C).	
B.		Humidity:	Up to 90% relative, non-condensing	
 
2.32	MECHANICAL SPECIFICATIONS

A.		Construction:	Aluminum 	
B.		Dimensions:	Height: 3.33 in. (84.61 mm).  
Width: 3.54 in (90 mm).
Depth: 11.83” (300.4 mm).	
C.		Weight:	2.32 lb (1.05 kg)	
D.		Camera Mount:	Indoor or outdoor. Surface mount with integral wall mount.	

2.33	CERTIFICATIONS

A.	CE
B.	UL 
C.	FCC, Class A
D.	IP66
E.	IK10

2.34	WARRANTY

A.	3 years, parts and labor 

2.35	APPROVED MANUFACTURERS

A.	The outdoor fixed color IP bullet camera shall be Vicon Industries Model Model V942B-W312MIR, V942B-W312MIR-XW, V942B-W312MIR-XS, V944B-W312MIR, and V945B-W310MIR.
B.	The fixed dome, day/night camera shall be available to be shipped pre-configured and programmed to the systems requirements by the manufacturer.

2.36	INDOOR FIXED IP DOME CAMERA

A.	The indoor fixed dome camera shall incorporate a camera/lens combination. The dome camera shall be available for indoor surface mounting. The high-resolution day/night camera shall have true WDR and IR capability and include an integral fixed or motorized varifocal autoiris lens. Day/night operation shall be achieved using a built-in IR-cut filter. IR distance shall be 82 ft (25 m) with 24 IR LEDs. A clear polycarbonate lower dome that is secured by tamperproof screws shall be included. 
B.	The camera position shall have a three-direction adjustment, allowing for adjustment of pan, tilt and lens rotation (roll), for any angle of view required.
C.	The dome camera shall have smart encoding, which monitors the amount of motion in a scene, resulting in overall savings in storage and bandwidth without sacrificing video quality.
D.	The dome camera shall be powered by PoE or 12 VDC. 
E.	The dome camera shall have quad streaming video and support H.264/H.265, and 
M-JPEG compression. The camera shall be available in 1080p (2 MP) and 4 MP resolution. 
F.	Camera features shall include electronic iris, WDR, digital zoom, white balance, flip and mirror, privacy masks, museum search and motion detection.
G.	The dome camera shall meet the FCC requirements for a Class A device. It shall include support for the industry-standard ONVIF interface.
H.	The dome camera shall provide a slot for an SD card for local storage.
I.	The fixed-position dome camera shall meet or exceed the following design and performance specifications.

2.38	DAY/NIGHT IP DOME CAMERA SPECIFICATIONS

A.	Imaging Device:	2 MP: 1/3-inch progressive scan CMOS; 
	4 MP: 1/2.8-inch progressive scan CMOS;
B.	Max. Resolution:	1080p (2 MP) and 4 MP models
C.	Shutter Speed:	1 - 1/10,000 sec
D.	Digital Zoom:	Yes
E.	Sensitivity:	Color: 0.1 lux; B&W: 0 lux (IR On) @f/2.1
F.	Tilt and Horizontal	3-axis adjustment: pan (360°), tilt (90°) and roll (lens Adjustment:	may be rotated on its axis 360°)
G.	Lens Adjustment:	Fixed or motorized focus and zoom adjustment 
H.	Focal Length:	Fixed models: 3.7 mm (2 MP); 3.6 mm (4 MP) 
	Motorized models: 2.8-12 mm varifocal
I.	Horizontal Field of View:	Fixed models: 90° (2 MP); 85° (4 MP)
	Motorized models: 100°- 30°
J.	IR Distance:	82 ft (25 m); 24 IR LEDs 

2.39	ELECTRICAL SPECIFICATIONS

F.	Input Voltage:	PoE, 12 VDC 
G.	Current (IR on):	PoE: 170 mA/180 mA (fixed); 620 mA (motorized)
                                             12 VDC: 190 mA (fixed); 680 mA/710 mA (motorized)
H.	Power Consumption 
(IR on):	PoE: 8.2 W/7.6 W (fixed); 8.2 W/8.5 W (motorized)
	12 VDC: 6.8 W (fixed); 7.4 W/7.6 W (motorized)
I.	Connectors:	Power: standard jack for adapter 
				PoE/Network: RJ-45
					Alarm: screw terminal
					Audio: screw terminal
					Slot for SD card
					Analog video output (requires optional cable)
J.	Radio Frequency	
Emission Rating: 		FCC Class A; CE

2.40	ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temperature:	14° to 140°F (-10° to 60°C) 
B.	Humidity:	Up to 90% relative, non-condensing

2.41	PHYSICAL SPECIFICATIONS
A.	Construction:	Plastic
Dome: clear polycarbonate; tamperproof screws
B.	Dimensions:	Height: 4.1 in. (104.1 mm), 
Diameter: 5.1 in. (130 mm)
C.	Weight: 	Fixed: 0.82 lb (0.375 kg); Motorized: 0.90 lb (0.4 kg)

2.42	MECHANICAL SPECIFICATIONS
A.	Camera Mount:	Surface mount 
B.	Adjustments:	3 axis adjustment, pan (360°), tilt (90°) and roll/azimuth (360°) 

2.43	NETWORK VIDEO SPECIFICATIONS
A.	Communication Platform:	Open platform; compatible with Valerus and ViconNet 
	Video Management Systems 
B.	Compression:	H.264/H.265; M-JPEG available 
C.	LAN Interface:	10 Base-T/100 Base-TX
D.	Video Channels	Quad streaming
E.	Resolution and Frame Rate:	1080p (2 MP): 1920x1080, 1440x1080, 
				1280x1024,1280x720/960 (720P), 1024x768, 
				704x480/576 (D1), 640x480 (VGA), 400x240, 
				320x240 (QVGA)
				4 MP: 2592x1520, 2304x1296, 1920x1080 (1080P), 
				1440x1080, 1280x1024, 1280x720/960 (720P), 
				1024x768, 704x480/576 (D1), 640x480 (VGA), 400x240, 
				320x240 (QVGA)
Max 30 fps at 1920x1080
F.	Web Browser:	Internet Explorer, Chrome, Safari, Firefox 
G.	Users:	Up to 10 clients
H.	Image Settings:	Day/night mode; flip and mirror; configurable 
                                             brightness, contrast, chroma, sharpness, saturation; 
	white balance; Electronic Shutter, automatic or manual;
                                             true WDR; privacy masks (4); motion detection (16); 
	DNR; digital zoom
I.	Video Content Analytics:	Defog, Intrusion Detection, Intelligent Video Motion 
	Detection, museum Search and Camera Tampering
J.	Supported Protocols:	IPv4/IPv6, TCP/IP, HTTP, HTTPS, RTSP, RTCP, RTP, 
                                             DHCP, FTP, UDP, uPnP,QoS, Zeroconfig, Bonjour

2.44	CERTIFICATIONS
A.	CE
B.	FCC, Class A

2.45	WARRANTY
A.	3 years, parts and labor

2.46	APPROVED MANUFACTURERS
A.	The indoor fixed color IP dome camera shall be Vicon Industries Model V802D-WIR, V802D-W312MIR, V804D-WIR and V804D-W312MIR.

2.37	OUTDOOR IP BULLET CAMERA 
A.	The outdoor bullet camera shall incorporate a camera/lens combination. The dome camera shall be available for surface mounting on an integral wall mount. The high-resolution day/night camera shall have WDR and IR capability and include an integral fixed or motorized varifocal autoiris lens. Day/night operation shall be achieved using a built-in IR-cut filter. IR distance shall be 98 ft (30 m). 
B.	The camera position shall allow for adjustment of angle of view on its integral wall mount. 
C.	The camera shall have smart encoding, which monitors the amount of motion in a scene, resulting in overall savings in storage and bandwidth without sacrificing video quality.
D.	The camera shall be powered by PoE or 12 VDC. 
E.	The camera shall have triple streaming video and support H.264/H.265, and 
M-JPEG compression. The camera shall be available in 1080p (2 MP) and 4 MP resolution. 
F.	Camera features shall include electronic iris, WDR, digital zoom, white balance, flip and mirror, privacy masks, museum search and motion detection.
G.	The camera shall meet the FCC requirements for a Class A device. It shall include support for the industry-standard ONVIF interface.
H.	The camera shall meet or exceed the following design and performance specifications.

2.47	DAY/NIGHT IP CAMERA DOME SPECIFICATIONS
A.	Imaging Device:	2 MP: 1/2.9-inch progressive scan CMOS; 
	4 MP: 1/3-inch progressive scan CMOS;
B.	Max. Resolution:	1080p (2 MP) and 4 MP models
C.	Shutter Speed:	1 - 1/10,000 sec
D.	Digital Zoom:	Yes
E.	Sensitivity:	Color: 0.1 lux; B&W: 0 lux (IR On) @f/2.1
F.	Tilt and Horizontal	Adjust camera position on integral wall mount. 
Adjustment:	Mechanical adjustment: pan (360°), tilt (90°) and	
	roll (360°)
G.	Lens Adjustment:	Fixed or motorized focus and zoom adjustment 
H.	Focal Length:	Fixed models: 3.6 mm 
	Motorized models: 2.8-12 mm varifocal
I.	Horizontal Field of View:	Fixed models: 84° 
	Motorized models: 95°- 35°
J.	IR Distance:	98 ft (30 m 

2.48	ELECTRICAL SPECIFICATIONS
A.	Input Voltage:	PoE, 12 VDC 
B.	Current (IR on):	PoE: 87 mA/106 mA (fixed); 280 mA (motorized)
                                             12 VDC: 145 mA (fixed); 520 mA/480 mA (motorized)
C.	Power Consumption 
(IR on):	PoE: 4.2 W/5.1 W (fixed); 7 W (motorized)
	12 VDC: 3.4 W/3.8 W (fixed); 6.2 W/5.8 W (motorized)
D.	Connectors:	Power: standard jack for adapter 
				PoE/Network: RJ-45
E.	Radio Frequency	
      Emission Rating: 	FCC Class A; CE

2.49	ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temperature:	14° to 122°F (-10° to 50°C) 
B.	Humidity:	Up to 90% relative, non-condensing

2.50	PHYSICAL SPECIFICATIONS
A.	Construction:	Aluminum
B.	Dimensions:	Fixed series: Length: 6.1 in. (155 mm), 
Diameter: 3.0 in. (77 mm)
Motorized Series: Length: 9.4 in. (239 mm), 
Diameter: 3.3 in. (84 mm)
C.	Weight: 	Fixed: 0.66 lb (0.3 kg); Motorized: 1.5 lb (0.68 kg)

2.51	MECHANICAL SPECIFICATIONS
C.	Camera Mount:	Integral wall mount for surface mounting 
A.	Adjustments:	Mechanical adjustment, pan (360°), tilt (90°) and roll/azimuth (360°) 

2.52	NETWORK VIDEO SPECIFICATIONS
A.	Communication Platform:	Open platform; compatible with Valerus and ViconNet 
	Video Management Systems 
B.	Compression:	H.264/H.265; M-JPEG available 
C.	LAN Interface:	10 Base-T/100 Base-TX
D.	Video Channels	Triple streaming
E.	Resolution and Frame Rate:	1080p (2 MP): 1920x1080, 1440x1080, 
				1280x1024,1280x720/960, 720P), 1024x768, 
				704x480/576 (D1), 640x480 (VGA), 400x240, 
				320x240 (QVGA)
				4 MP: 2592x1520, 2304x1296, 1920x1080 (1080P), 
				1440x1080, 1280x1024, 1280x720/960 (720P), 
				1024x768, 704x480/576 (D1), 640x480 (VGA), 400x240, 
				320x240 (QVGA
Max 30 fps at 1920x1080; 20 fps @ 4 MP
F.	Web Browser:	Internet Explorer, Chrome, Safari, Firefox 
G.	Users:	Up to 10 clients
H.	Image Settings:	Day/night mode; flip and mirror; configurable 
                                             brightness, contrast, chroma, sharpness, saturation; 
	white balance; Electronic Shutter, automatic or manual;
                                             true WDR; privacy masks (4); motion detection (16); 
	DNR; digital zoom
I.	Video Content Analytics:	Defog, Intrusion Detection, Intelligent Video Motion 
	Detection, Museum Search and Camera Tampering
J.	Supported Protocols:	IPv4/IPv6, TCP/IP, HTTP, HTTPS, RTSP, RTCP, RTP, 
                                             DHCP, FTP, UDP, uPnP,QoS, Zeroconfig, Bonjour

2.53	CERTIFICATIONS
A.	CE
B.	FCC, Class A

2.54	WARRANTY
A.	3 years, parts and labor

2.55	APPROVED MANUFACTURERS
A.	The indoor fixed color IP dome camera shall be Vicon Industries Model V812D-WIR, V812D-W312MIR, V814D-WIR and V814D-W312MIR.
2.38	NETWORK PTZ CAMERA DOME 

A.	The compact network dome shall be comprised of a camera/lens and pan/tilt drive in an attractive covert enclosure. It shall be have 1080p (2 MP) resolution.
B.	The network dome shall be shall provide network video transmission using either open platform H.264 or M-JPEG compression. The dome shall support ONVIF open architecture connectivity to enable third party software recording. The camera dome shall transmit high quality video across the network for remote viewing and recording and shall be configurable remotely from network digital video recorders and master workstations
C.	An alarm input shall be programmable for functional state (enabled or disabled); it shall be able to be set for Normally Open (NO) or Normally Closed (NC) and a dwell time shall be programmable from 1-180 second. The alarm output shall be able to control external equipment; it shall be able to be set for Normally Open (NO) or Normally Closed (NC). An audio alert shall be available.
D.	There shall be 256 individual programmable preset positions available. Each preset shall be able to have an individual title and shall be adjustable for pan and tilt speed and manual or auto focus.
E.	There shall be eight tours available with up to 100 presets per tour. Each tour shall be able to have an individual title and shall be adjustable for pan, tilt and zoom speed and dwell time. Tours shall be able to be programmed to repeat.
F.	Pan and tilt functions shall be programmable. Maximum manual pan and tilt speeds shall be programmable. Maximum pan speed shall be 380 degrees/sec and maximum tilt speed shall be 380 degrees/sec. Pan and tilt speeds shall also be scalable to the zoom setting. The pan range shall be 360 degree continuous and tilt range shall be 100 degrees (-10 to 90 degrees).
G.	The camera/lens shall be 1080p 1/2.8-in. progressive scan CMOS true day/night (IR cut filter) with a 4.3-129 mm varifocal lens (optical 30x). The camera shall feature true wide dynamic range (120 dB) to provide the highest quality image with excellent contrast.
H.	 The camera shall provide synchronized IR illuminators with 1312 ft (400 m) range.
I.	The camera shall provide high level, programmable functions. Configuration of the dome shall be done through a web browser. There shall be a dynamic adjustable bit rate. Brightness, sharpness and high-sensitivity shall be configurable. The gain control shall be adjustable. The shutter speed shall be programmable, automatic or manual. The camera shall have white balance gain using red and blue scales. Backlight compensation or Wide Dynamic Range shall be programmable. Horizontal flip shall be available. There shall be Dynamic Noise Reduction control. Video Content Analysis (VCA) shall be provided for tampering, defog, digital image stabilization, face detection, line detector and field detector.
J.	The rugged PTZ housing shall be constructed of die-cast aluminum; it shall be secured with tamperproof screws. A wall mount and a ceiling/pole mount shall be available. The camera dome shall have an IP66 and IK10 rating. The camera shall provide a Micro SD card slot for local storage.
K.	An event map shall be available to establish a schedule for each event trigger from the camera; up to 15 events shall be able to be registered.
L.	12 individual programmable privacy masks shall be available to hide certain areas for display on screen.
M.	Motion detection capability shall be available. There shall be 16 configurable zones for motion detection. Each zone shall be individually configurable for threshold, sensitivity and dwell time levels. 
N.	The capability to flip (invert) the video image shall be available. This feature is useful when mounting units in an inverted position.
O.	The dome shall have a maximum video transmission rate of 30 fps (25 fps PAL).
P.	Two-way audio shall be provided.
Q.	The dome shall be capable of 10 simultaneous viewing/recording streams per camera.

2.39	NETWORK VIDEO TRANSMISSION

A.	Communication Platform: 	Open platform; compatible with Vicon Valerus/ViconNet Digital Video Management System 
B.	Compression:		H.264, M-JPEG
C.	Video Output:		1080p: 1920 x 1080 @ 30 fps
D.	Protocols:		IPv4/IPv6, HTTP, HTTPS, RTSP/RTP, RTCP, FTP, SMTP, UPnP, TCP/IP, DHCP, UDP, NTP, DDNS, Zeroconfig, Bonjour, ONVIF

2.40	CAMERA SPECIFICATIONS

A.	Imaging Device:		1/2.8-inch progressive scan CMOS
B.	Maximum Resolution:	1080p 1920 x 1080 
C.	Shutter Speed:		1/3 to 1/10,000 sec
D.	Gain Control:		Automatic/Manual
E.	WDR	:	On/Off selectable; 120 dB
F.	Backlight Compensation:	On/Off selectable 
G.	Sensitivity:	Color: 0.35 lux; B&W: 0.013 lux, IR LED On @50 IRE; 0 lux, IR LED On.
H.	Iris Control:		Automatic/Manual
I.	Video Focus:		Automatic/Manual
J.	White Balance:		Automatic/Manual; red/blue gain adjustable
K.	Digital Zoom:		16X
L.	Lens:		4.3 – 129 mm (30X optical zoom), f/1.2; 
                    2° – 65° horizontal angle of view

2.41	ELECTRICAL SPECIFICATIONS

A.	Input Voltage:	12 VDC; PoE+ (injector included).
B.	Current (IR On):	2.3 A @ 12 VDC; 500 mA @ PoE
C.	Power Consumption:	28 W.
D.	Power Connector:	12 VDC jack
E.	Network Connector:	RJ-45 CAT 5
F.	Audio Connector:	Jack; audio out requires external amplifier
G.	Alarm Inpu/Output:	Screw terminal block (4 alarm in/1 alarm out)
H.	Video Out:	RJ-45 connector
I.	Relay:	4-position removable screw terminal block.
J.	Radio Frequency	
Emission Rating: 		FCC Class A
2.42	ENVIRONMENTAL SPECIFICATIONS

A.	Operating Temperature:	-22° to 149°F (-30° to 65°C) 
B.		NEMA 2.1.5.1 STD2.

2.43	PHYSICAL SPECIFICATIONS

A.	Dimensions:		Width: 7.9-in. (201 mm).
                                Height: 14.6-in. (371 mm).
B.	Weight: 			10.8 lb (4.9 kg).

2.44	MECHANICAL SPECIFICATIONS

A.	Application:		Outdoor; IP66, IK10
											
2.45	CERTIFICATIONS

A.	FCC, Class A
B.	CE
C.	ONVIF 

2.46	WARRANTY
A.	3 years, parts and labor 

2.47	APPROVED MANUFACTURERS

A.	The camera dome shall be Vicon Industries Model SN680D-B-WNIR dome camera.

2.56	NETWORK OUTDOOR CAMERA DOME FEATURES
A.	The compact network dome shall be comprised of a high-resolution camera/lens and pan/tilt drive in an attractive covert enclosure. The outdoor model shall be available with 1080p (2 MP) resolutions.

B.	The network dome shall be designed for easy installation. The lower dome shall be constructed of impact-resistant polycarbonate and is secured by tamperproof screws. Several mounting options shall be available.

C.	The network dome shall be shall provide triple-streaming network video transmission using open platform H.264 or M-JPEG compression (2x H.264 and 1x M-JPEG). The dome shall support ONVIF open architecture connectivity to enable third party software recording. The camera dome shall transmit high quality video across the network for remote viewing and recording and shall be configurable remotely from network digital video recorders and master workstations.

D.	Four alarm inputs shall be individually programmable NO or NC. There shall be one alarm output. 

E.	There shall be 256 individual programmable preset positions available. The dome shall have a 360 degree continuous pan range and 180 degree tilt range with digital flip.

F.	There shall be 8 tours available with up to 100 presets per tour. 

G.	Maximum pan speed shall be 380 degrees/sec and maximum tilt speed shall be 380 degrees/sec on preset. Variable speed shall be 0.1°/sec to 380°/sec. 
H.	The camera/lens shall be a 1/2.8-in. progressive scan CMOS day/night with a 4.7-94 mm varifocal lens (optical 20x; 16X digital zoom). The camera shall feature true wide dynamic range to provide the highest quality image with excellent and electronic image stabilization.

I.	The camera shall provide high level, programmable functions. Configuration of the dome shall be done through a web browser. The gain control shall be adjustable. The shutter speed shall be automatic or manual. The camera shall have white balance gain using red and blue scales. Backlight compensation or Wide Dynamic Range shall be programmable. Digital Noise Reduction shall be programmable on or off.
J.	The camera dome shall be surface mountable; wall, corner and pole mounting accessories shall be available.
K.	A real time clock and scheduler shall be available. Recording schedules shall be programmable for each day of the week. Up to 15 events shall be programmable and a schedule shall be able to be established for each event trigger.
L.	8 programmable privacy masks shall be available.
M.	Motion detection capability shall be available. There shall be 16 windows for motion detection (8 include, 8 exclude). Each window’s sensitivity level shall be programmable. 
N.	The capability to digitally flip (invert) the video image shall be available. This feature is useful when mounting units in an inverted position.
O.	Multilanguage menu system shall be provided.
P.	The dome shall have a maximum video transmission rate of 60 fps (triple stream) and 30 fps (dual stream).
Q.	Audio input shall be provided. There shall be 1 audio in and 1 audio out.
R.	The dome shall be capable of 10 simultaneous live viewing streams (live) and 3 playback streams per camera.
S.	A micro-SD memory slot shall be available for local storage.

2.38	NETWORK VIDEO TRANSMISSION
A.	Compression:		H.264, M-JPEG
B.	Video Output:		1920 x 1080 @ 30 fps
C.	Programming Interface:	ONVIF Profile S, NTCIP 
D.	Protocols:		IPv4/IPv6, HTTP, HTTPS, RTSP/RTP, RTCP, FTP, uPnP, TCP/IP, DHCP, UDP, ARP, QoS, Zeroconfig, Bonjour

2.39	CAMERA SPECIFICATIONS
A.	Imaging Device:		1/2.8-inch progressive scan CMOS
B.	Shutter Speed:		1/3 to 1/30,000 sec
C.	Gain Control:		Automatic/Manual
D.	WDR	:	120 dB; WDR On/Off selectable
E.	Backlight Compensation:	On/Off selectable 
F.	Sensitivity:	Color: 0.35 lux;
B&W: 0.13ux, @ 50IRE
G.	Iris Control:		Automatic/Manual
H.	Video Focus:		Automatic/Manual (near-far)
I.	White Balance:		Automatic/Manual; red/blue gain adjustable
J.	Digital Noise Reduction:	Programmable On/Off
K.	Lens:		4.7 – 94 mm; 
                    55.3° – 3° horizontal angle of view

2.40	ELECTRICAL SPECIFICATIONS
A.	Input Voltage:	PoE; 24 VAC; 12 VDC. 
B.	Power Consumption:	12 W max
C.	Power Connector:	2-position removable screw terminal block 
D.	Network Connector:	RJ-45 CAT 5
E.	Audio Connector:	2 1/8-in. phono jacks
F.	Alarm Input:	8-position removable screw terminal block
G.	Video Out:	RJ-45 connector
H.	Relay:	4-position removable screw terminal block.
I.	Radio Frequency	
      Emission Rating: 		FCC Class A

2.41	ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temperature:	-40° to 1652°F (-40° to 74°C) in accordance with 
				NEMA 2.1.5.1 STD2.

2.42	PHYSICAL SPECIFICATIONS
A.	Dimensions			Diameter: 6.1-in. (154 mm).
Height: 5.9-in. (1502 mm).
Lower Dome
4.3-in. (110 mm) 
B.	Weight: 			3.5 lb (1.6 kg).

2.43	MECHANICAL SPECIFICATIONS
A.	Application:	Outdoor; IP66

2.44	CERTIFICATIONS
A.	UL
B.	FCC, Class A
C.	CE
D.	ONVIF Profile S compliant

2.45	WARRANTY
A.	3 years, parts and labor 
2.46	APPROVED MANUFACTURERS
A.	The camera dome shall be Vicon Industries Model Cruiser SN673V-B

2.47	IP BOX CAMERA 

A.	The indoor box camera shall be available without a lens or incorporate a camera/lens combination; a motorized varifocal lens shall be available as well as a model with no lens which will accept a CS-mount lens. The high-resolution day/night camera shall be available with an integral 2.8-12 or 2.8-8.5 mm motorized zoom and focus varifocal lens. Day/night operation shall be achieved using a built-in IR-cut filter. Wide Dynamic Range (WDR) shall be available on the 1 MP and 2 MP models.
B.	The box camera shall be powered by PoE, 24 VAC or 12 VDC. 
C.	The box camera shall have simultaneous dual streaming video and support H.264 and M-JPEG compression. The camera shall be available in 4 resolutions, 1 MP (720p), 2 MP (1080p), 3.1/3.8 MP and 5 MP.
D.	Two-way audio shall be available as well as an on-camera microphone. Alarm I/O relay shall be available as well as analog video out.
E.	Camera features shall include AGC, BLC, white balance, automatic exposure, electronic shutter, flip and rotate 180°, privacy masks, and motion detection.
F.	The box camera shall meet the FCC requirements for a Class A device. It shall include support for the industry-standard ONVIF interface and PSIA. 
G.	The box camera shall provide a slot for an SD card for local storage.
H.	The box camera shall meet or exceed the following design and performance specifications.

2.48	DAY/NIGHT IP BOX CAMERA SPECIFICATIONS

A.	Imaging Device:	1/2.7-inch (1MP and 2MP)1/3.2-inch (3MP and 5MP)
B.	Max. Resolution:	1 megapixel (720p); 2 megapixel (1080p), 
                                       3.1/3.8 megapixel and 5 megapixel models
C.	Shutter Speed:	Auto/Programmable/Fixed
D.	Automatic Gain Control:	On/Off selectable
E.	Sensitivity:	Color: 1-2 MP: 0.1 lux; 3-5 MP: 0.2 lux; 
                                       B&W: <0.05 lux 
F.	Tilt and Horizontal	Dependent on mount
G.	Lens Adjustment:	Motorized zoom and focus and P-iris
H.	Focal Length:	2.8-12 mm or 2.8-8.5 mm varifocal
I.	Horizontal Field of View:	2.8-12 mm: 101°- 35°; 2.8-8.5 mm 93°- 44° 

2.49	ELECTRICAL SPECIFICATIONS

A.	Input Voltage:	PoE; 12 VDC; 24 VAC
B.	Power Consumption:	<4 W
C.	Connectors:	Power: PoE RJ-45 
					Video/Data: RJ-45
					Push-in terminal for I/O relay; audio in/out; analog output
					Slot for SD card
D.	Radio Frequency	
      Emission Rating: 		FCC Class A; CE

2.50	ENVIRONMENTAL SPECIFICATIONS

A.	Operating Temperature:	-32° to 113°F (0° to 45°C) 

2.51	PHYSICAL SPECIFICATIONS

A.	Construction:	Aluminum and plastic
B.	Dimensions:	Height: 2.76 in. (70.2 mm),
Width: 2.72 in. (69 mm),
Length: 5.07 in. (128.9 mm) 
C.	Weight: 	Approximately 0.4 lb (0.165 kg)

2.52	MECHANICAL SPECIFICATIONS

A.	Camera Mount:		¼-20 mounting holes, top and bottom 

2.53	NETWORK VIDEO SPECIFICATIONS

A.	Communication Platform:	Open platform; compatible with Vicon Valerus and ViconNet Digital 
	Video Management System, ONVIF/PSIA 
B.	Compression:	H.264; MPEG-4; M-JPEG available
C.	LAN Interface:	10 Base-T/100 Base-TX, Multicast
D.	Video Channels	Dual streaming
E.	Max. Resolution/Frame Rate:720p: 1280x720
1080p: 1920x1080
3.1 MP: 2048x1536
5 MP: 2592x1944
1, 2 MP: 30 fps; 3.1 MP: 20 fps; 5 MP: 15 fps
F.	Web Browser:	Internet Explorer, Firefox, Chrome, Safari, Mozilla, 
	Opera
G.	Users:	Live viewing for up to 10 clients
H.	Image Settings:	Auto exposure; configurable brightness, contrast, saturation, and
	sharpness; auto white balance, AGC; BLC; 
                                             motion detection; AC lighting control (50/60 Hz)
I.	Supported Protocols:	TCP/IP, HTTP, HTTPS, RTSP, RTP, CIFS, 
                                             SMTP, DHCP, NTP, DNS, UDP, uPnP, ARP, 
                                             SNMP, ICMP, Zeroconf, APIPA, Telnet, multicast. 
                                             IPV4, IPV6 (available with firmware update)

2.54	CERTIFICATIONS
A.	CE
B.	UL, cUL
C.	FCC, Class A
D.	RoHS 2
E.	ONVIF
F.	PSIA

2.55	WARRANTY
A.	3 years, parts and labor

2.56	APPROVED MANUFACTURERS

A.	The IP box camera shall be Vicon Industries Models IQB91WI-A5, IQB92WI-A5, IQB93NI-NL, IQB93NI-A6, IQB95NI-NL and IQB95NI-A6. Models with A5 and A6 have a motorized varifocal lens.
B.	An IR accessory shall be available, model IQB9-IR. A PoE housing shall be available, model 
HPOE-100.

2.57	PANORAMIC 360° CAMERA 

A.	The hemispheric camera dome shall be available in 6 MP and 12 MP indoor and outdoor models. It shall incorporate a fixed camera/lens combination. The camera dome shall be available for surface mounting; other mounting options shall be available. The high-resolution day/night camera shall have WDR and Smart IR capability and be include an integral fisheye lens. This lens shall provide an extremely wide angle of view for a panoramic image, capturing a complete 360° view. Day/night operation shall be achieved using a built-in IR-cut filter. IR distance shall be 16 ft (5 m) for the indoor and outdoor models. 
B.	The camera shall provide a high-resolution hemispherical view and shall provide crisp distortion free images. The camera shall offer both server-based dewarping at 12 MP and edge-based dewarping at 4 MP.
C.	The camera dome shall be powered by PoE or 12 VDC. 
D.	The camera dome shall have simultaneous dual streams video based on two configuration in single view mode; multiple streams based on single configuration in 6 cropped VGA mode shall also be available. The camera shall support H.264 and M-JPEG compression. The camera shall be provide 6 megapixel resolution.
E.	Camera features shall include electronic iris; configurable brightness, contrast, saturation; white balance; AGC; BLC; motion detection; privacy masks; smart text overlay; smart events.
F.	The camera dome shall meet the FCC requirements for a Class A device. It shall include support for the industry-standard ONVIF interface. The outdoor model shall be IP66-rated to withstand rain, dust and vandalism; both indoor and outdoor models shall be IK10 rated.
G.	The camera dome shall provide a slot for an SD card for local storage.
H.	The hemispheric camera dome shall meet or exceed the following design and performance specifications.

2.58	PANORAMIC 360° CAMERA SPECIFICATIONS

A.	Imaging Device:	6 MP: 1/1.8-inch progressive scan CMOS; 
                                             12 MP: 1/1.7-inch progressive scan CMOS 
B.	Max. Resolution:	6 MP and 12 MP models.
C.	Shutter Speed:	1 - 1/10,000 sec; Extreme l: 1/5 - 1/2000 sec
D.	Sensitivity:	6 MP: Color: 0.04 lux; B&W: 0.002 lux;
12 MP: Color: 0.1 lux; B&W: 0.01 lux
E.	Digital Zoom:	Yes 
F.	Lens Adjustment:	6 MP: Fixed lens, F1.6; M12 lens mount 
                                             12 MP: Fixed lens, F2.8; M12 lens mount
G.	Focal Length:	6 MP: 1.6 mm; 12 MP: 1.65 mm.
H.	Angle of View:	6 MP: 185° at full resolution 
                                             12 MP: 1905° at full resolution
I.	IR Distance:	16 ft (5m), 850 nm. 

2.59	ELECTRICAL SPECIFICATIONS

A.	Input Voltage:	Input Voltage:	12 VDC or PoE
B.	Current (IR on):	PoE: 0.14 A; 
                                              12 VDC: 0.675 A.  
C.	Power Consumption 
(IR on):	PoE: 9  W; 
                                             12 VDC: 10 W; 
D.	Connectors:	Power: 12 VDC screw terminal or 
				PoE RJ-45
					Video/Data: RJ-45
					Alarm: screw terminal
					Audio: screw terminal (indoor); jack (outdoor)
					Slot for SD card
E.	Radio Frequency	
Emission Rating: 		UL; FCC Class A; CE

2.60	ENVIRONMENTAL SPECIFICATIONS

A.	Operating Temperature:	Indoor: 14° to 122°F (-10° to 50°C);
                                             Outdoor: -22° to 122°F (-30° to 50°C) 
B.	Humidity:	Up  to 90% relative, non-condensing
C.	Ratings:	IP66 (outdoor)/IK10

2.61	PHYSICAL SPECIFICATIONS

A.	Construction:	Aluminum.
B.	Dimensions:	Outdoor: Height: 2.17 in. (55 mm), 
Diameter: 4.6 in. (117 mm) 
C.	Weight: 	0.88 lb (0.40 kg).

2.62	MECHANICAL SPECIFICATIONS

A.	Camera Mount:		Surface mount; mounting options available. 

2.63	NETWORK VIDEO SPECIFICATIONS

A.	Communication Platform:	Open platform; compatible with Vicon Valerus and ViconNet Digital
                                             Video Management System 
B.	Compression:	H.264; M-JPEG 
C.	LAN Interface:	10 Base-T/100 Base-TX, Unicast/Multicast
D.	Video Channels	Quad streaming
E.	Resolution and Frame Rate:	6 MP or 12 MP (model dependent); up to 60 fps depending of video
                                             streaming and resolution.
F.	Web Browser:	Internet Explorer 7.0 and above, Safari, Firefox
G.	Users:	Up to 20 clients.
H.	Image Settings:	Configurable brightness, contrast, hue, sharpness. 
	saturation; white balance; WDR; exposure; edge 
	dewarping; DNR; privacy masks; ICR; BLC; digital zoom; 
                                             motion detection.    .
I.	Supported Protocols:	IPv4/IPv6, TCP/IP, HTTP, HTTPS, RTSP, RTP 
                                             SMTP, DHCP, PPPoE, IGMP, FTP, UDP, 
	uPnP, QoS, SNMP ARP, ONVIF.

2.64	CERTIFICATIONS

A.	UL
B.	CE
C.	FCC, Class A
D.	IP66 (outdoor)
E.	IK10

2.65	WARRANTY
A.	3 years, parts and labor

2.66	APPROVED MANUFACTURERS

A.	The outdoor hemispheric IP dome camera shall be Vicon Industries Model V9360W-6 (6 MP) and Model V9360W-12 (12 MP); the indoor model shall be Model V9360-6 (6 MP) and V9360-12 (12 MP).

2.67	CORNER-MOUNTED CELL CAMERA

A.	The indoor high-security camera shall incorporate a housing, camera, lens and 36 IR illuminators; the brightness of the IR illuminators shall be adjustable. Its design shall be specifically for use in custodial suites and prison cells. The high-resolution day/night camera shall be available with an integral 
2.3 mm wide angle lens.

B.	The camera shall be waterproof and shall fit into a 90° corner. It shall consist of a two part stainless steel assembly, a fixed mounting frame and a removable front plate. The front plate shall be recessed and secured to the fixed frame with security screws. The front plate shall have two 5 mm thick windows to protect the camera and IR LED illuminators. Once installed, it shall be able to be permanently sealed to the wall to make the housing ligature proof.

C.	The camera shall support proprietary H.264, MPEG-4 and M-JPEG compression. 

D.	The camera shall have an adjustable mount that shall allow it to be tilted up or down for an exact view.

E.	The camera shall be powered by PoE, 12 VDC or 24 VAC.

F.	The camera shall provide alarms and audio. Privacy masks shall be available. A Micro SD slot shall be available for local storage.

G.	The camera shall meet or exceed the following design and performance specifications.

2.68	DAY/NIGHT CAMERA SPECIFICATIONS

A.	Imaging Device:	1/2.8-inch CCD 
B.	Resolution:	3 MP 
C.	Camera Type:	True day/night
D.	Sensitivity:	0.0 lux, IR On
E.	Lens:	Focal Length: 2.3mm
Horizontal Field-or-View: 124°
Vertical Field-or-View: 92°

2.69	NETWORK VIDEO TRANSMISSION

A.	Compression:	H.264, MPEG-4 or M-JPEG
B.	Video Streams:	10 concurrent streams mas.
C.	Resolution:	3 MP
D.	Frame rate:	Up to 30 fps

2.70	ELECTRICAL SPECIFICATIONS

A.	Input Voltage:	24 VAC, 12 VDC or PoE
B.	Current @ IR On:	24 VAC/12 VDC: 500 mA; PoE (48 VDC): 125 mA
C.	Power Consumption:	6 W max
D.	Connectors:	Power: 12 VDC/24 VAC: screw terminal; PoE/Ethernet: RJ-45;
	Alarms (In/Out): screw terminal; Audio (mic/spkr): screw 
	terminal; Micros SD card slot. 
E.	Radio Frequency	
      Emission Rating: 		FCC Class A

2.71	ENVIRONMENTAL SPECIFICATIONS

A.	Operating Temperature:	32° to 140°F (0° to 60°C)

2.72	PHYSICAL SPECIFICATIONS

A.	Application:	Indoor
B.	Construction:	Enclosure: stainless steel; brushed satin
				Window: polycarbonate
C.	Mounting:	Designed to be mounted into a 90° corner; front cover 
				secured with security screws
D.	Dimensions:	15 in. (380 mm) x 12.6 in. (320 mm)
	
E.	Weight: 	Approximately 3.5 lb (1.6 kg)

2.73	CERTIFICATIONS

A.	FCC, Class A
B.	CE
C.	UL/CUL
D.	IP66
E.	IK10

2.74	WARRANTY

A.	3 years, parts and labor

2.75	APPROVED MANUFACTURERS

A.	The corner-mount IP cell camera shall be Vicon Industries Model Roughneck V-CELL-HD-B.

END OF SECTION

Vicon, Roughneck and Valerus are registered trademarks of Vicon Industries, Inc in the United States and other countries.
Microsoft and Microsoft Windows are registered trademarks of Microsoft Corporation in the United States and other countries.
Intel and Core are trademarks or registered trademarks of Intel Corporation.