TECHNICAL SPECIFICATIONS 				SECURITY SYSTEM
DIVISION 13 - SPECIAL CONSTRUCTION
SECTION 137_ _ - SECURITY CCTV SYSTEM

PART 2 - PRODUCTS
2.01 GENERAL
A. All equipment and materials used shall be standard components, regularly manufactured, 
regularly utilized in the manufacturer’s system.
B. All systems and components shall have been thoroughly tested and proven in actual use.
C. All systems and components shall be provided with the availability of a toll free 24-hour technical 
support phone number from the manufacturer. The phone number shall allow for immediate 
technical assistance for either the dealer/installer or the end user at no charge.
D. All systems and components shall be provided with an explicit manufacturer warranty.

2.02 UNINTERRUPTIBLE POWER SUPPLY
A. These shall be self contained uninterruptible power supplies that feature transparent power backup for all 120 VAC devices and provide surge protection. In addition, all shall provide an automatic self-test, shall be cold-start capable, shall have hot-swappable batteries and shall sound an audible alarm. 
B. There shall be 4 versions of uninterruptible power supplies, with 725 VA, 1000 VA and 3000 VA 
output power. The 1000 VA version shall have both a standalone and a rack mount model; the 
3000 VA model shall be a rack mount model. 
C. These UPS units are managed by PowerChute® plus software. PowerChute plus allows users to 
customize UPS response to power events. A variety of responses can be chosen to react to a power 
or environmental event, including a safe, automatic shutdown and reboot to protect against crashes 
and security violations.
D. Backup time at full load for the 725, 1000, 1000 rack version and 3000 VA shall be 4.3, 9.6, 8.8, 
14.1 minutes; at half load it shall be 14, 33.3, 29.9 and 33.9 minutes.
E. The 725 VA UPS shall comply with requirements for an FCC Class B device; the 1000 VA and 
3000 VA versions shall comply with requirements for an FCC Class A device.

The uninterruptible power supplies shall be Vicon Industries models V725-UPS, V1000-UPS, V1000R-UPS and V3000R-UPS.

Spec V147-01-00